## Sheet1 (hidden)
IOM International Organization for Migration

## Rehab. of Jebal Moya WTP
Bill of Quantities ( BOQ) 1
Project Name : Sudan Integrated Social Sector Infrastructure Rehabilitation Project (SISSIRP) Project Type : WASH Project Locations: Sennar, Sennar, Rehabilitation of Jebal Moya WTP- Banant Alnifdia Project Duration: days
General Guidelines
1 | Drawings and BoQ are complementary to each other, hence the contractor has the obligation to execute the tasks mentioned in either one of them. Accordingly The contractor's shall include all what is mentioned in the drawings & all what is mentioned in the BOQs. Incase BOQ and technical drawings have discrepancies. BOQ supersedes technical drawings. Follow IOM site engineers site instruction at all times.
2 | All the BoQ articles comprise supplying manpower, machinery, equipment, transportation all necessary requirements to get the work done properly regardless of it's mentioned in the BoQ articles or not.
3 | In case that there is any item or detail in the drawings not mentioned in the BOQ (or vise versa) then this item or detail is considered included in the contractor's price for this project & he should execute it within his contract price without claiming any increase to the contract price, as it is considered part of the contract.
4 | All the BoQ articles must be carried out according to the guidelines of Sudanese Technical Specifications, with updates and instructions of IOM Engineer.
5 | All the BoQ articles comprise removing and transporting any debris or rubble to allocated disposal areas by municipality or local authority.
6 | The Contractor must obtain prior written approval from the IOM Programme Manager and the Procurement Unit for any cost-related Variation Orders. IOM Engineer will record and justify any variations to both parties. No VO shall be implemented without the Programme Manager's written approval.
7 | Site visit is required for vendor to see / inspect project, and to submit a letter mentioning site been visited with tendering documents.
8 | Follow IOM Engineer's instruction at all times.
9 | Submit work plan schedule for project activities.
Technical Specifications:
1 | The price includes all required materials, fittings , accessories , tools , machines , instruments, labor works with all the requirements, installing , testing and commissioning and put in operation to get the system work properly as per international specifications , beneficiary and IOM engineer instructions and to complete the works as stated in the contract items , shop drawings , details and complete the work in all aspects.
2 | Supplying of materials shall not be done before getting IOM Engineer's approval on the materials type, also the contractor should provide certificate of origin and tests result certificate for the supplied materials
3 | All materials should be a good quality and the brand and origin should be subject to the approval of IOM Engineer . Show sample for IOM Engineer's approval before installing. Cost include transportation and installation. Follow IOM Engineer's instruction during installation.
4 | Any damaged parts in any system or structure due to the work in the site , will be responsibility of contractor to redo poor workmanship without cost to IOM .
5 | Contractor / vendor is responsible to delivered all the works to local authority,beneficiary as well as IOM Engineer.
6 | Curing for all concrete works should be maintained 24 hours, the curing should be not less than 7 days before construction start on top any concrete structure
7 | Cleaning the site from any debris during and after complete all the work.
8 | The Contractor shall equip all materials, workers and equipment necessary for the performance of the work specified in the Bill of Quantities and Drowings in all its aspects.
9 | All Electrical connection shall be tested and commissioned before handover to IOM Engineer
10 | The company will be responsible for getting all approval of his documents from the government authorities in the State
11 | All the fees for materials transport handling and testing of samples should be paid by the Contractor if it mentioned in the BoQ or not.
12 | The Contractor implementing this project should hire laborers and workers from the locality as much as possible.
# | Description of Work | Unit | Quantity | Unit Rate USD | Amount USD | Remarks
1 | General
A | Mobilization and Demobilization
A.1 | Mobilization and demobilization of the contractor’s personnel, specialized equipment, tools, lifting devices, transport vehicles, and temporary facilities required for the execution of mechanical, civil, and electrical works under this contract. The item shall include transportation of pumps, motors, installation equipment, welding machines, generators, lifting cranes/chain blocks, testing instruments, and all related tools to and from the project site; establishment of temporary site facilities; provision of supervision and logistics; and final demobilization upon completion of the works. The rate shall also include removal of temporary structures, clearing of the site, and restoration of the work area to its original condition to the satisfaction of the Engineer. | L.S | 1
B | Rehabilitation of River Intake / WTP Yard (Southeast Side)
B.1 | Rehabilitation of two (2) existing sluice gates (penstocks), each measuring approximately 1.50 m wide × 2.60 m high. The work shall include cleaning and checking all metal parts, applying three coats of suitable anti-rust paint, checking and securing all fittings, and greasing the threaded and moving parts to ensure smooth operation. The rate shall include all labour, materials, tools, and equipment required to complete the work and leave the sluice gates in good working condition. | L.S | 1
B.2 | Desilting and removal of all silt and sediment deposits around the water intake gate in all directions, including the area in front of the two gates, down to the full design depth also desilting and cleaning of two Sluice gate chambers : dimensions= 3.0m (length)x 2.0m (width)x 1.5m (depth).. The work shall include Dewatering, excavation/dredging, removal, transportation, and disposal of the dredged material at an approved location, and all incidental works necessary to restore the intake to its intended operating condition and ensure unobstructed water flow. | L.S | 1
B.3 | Rehabilitate the chamber walls by repairing all structural and non-structural cracks, replacing missing or deteriorated masonry units, and re-pointing/re-plastering with cement-sand mortar to restore the chamber to its original structural integrity. Supply, fabricate, and install a galvanized welded wire mesh cover mounted on a rigid 1½-inch galvanized mild steel angle frame with two daigonal bracing, complete with two lockable hinged access panels, anchor bolts, hinges, 96 mm two locking devices, and all necessary fittings. The work shall include surface preparation, fabrication, installation, corrosion protection, and all works required. | L.S | 1
B.4 | Supply, construct, and install stone masonry pitching/riprap in C/S mortar in front of the northern and southern chambers to provide erosion protection. The pitching shall cover an area of 3.0 m × 2.0 m with a thickness of 0.50 m at each location and shall include excavation, Subgrade preparation in a water-filled canal, supply of approved stone, cement mortar, joint filling, curing, and all works necessary to complete the installation in accordance with the Engineer's approval starting from the bottow edge of the intake pipe. | M3 | 6
B.5 | Construct an embankment measuring 30.0 m (L) × 4.0 m (W) × 1.0 m (average height) using approved selected fill material. The fill shall be placed in uniform layers not exceeding 200 mm in thickness and compacted mechanically. The work shall include site preparation, hauling, spreading, moisture conditioning, compaction, trimming to the required levels and slopes. | M3 | 120
C | WTP Yard and Fence
C.1 | Initial site preparation, including clearing and cleaning of the Water Treatment Plant (WTP) yard including removal of all grass, bushes, shrubs and cutting trees and unused equipments. The item shall include collection, loading, transportation, and safe disposal of all waste generated from this process at an approved and authorized local dumping site, (to be assessed during site visit). | L.S | 1
C.2 | Rehabilitate the existing perimeter fence by securing steel angle posts in concrete (40×40×40 cm, 1:3:6 mix), replacing defective posts where required, realigning sections, and tensioning/re-fixing chain-link mesh to restore full fence functionality. All works and quantities to be confirmed on site prior to execution. The item also includes supply and installation of five (5) steel angle posts (2" × 5 mm), complete with excavation, concrete foundations, bracing, mesh fixing, anti-rust primer, and two finishing paint coats. In addition, fabricate and install one (1) steel gate at the eastern side, size 1.0 m × 1.9 m, matching old existing gate material and section, complete with frame, hinges, locking system, welding, corrosion protection, and final paint finish, as approved by the Engineer (to be assessed during site visit). | L.S | 1
C.3 | Construction of a complete Gate including the supply of all materials, labour, tools, equipment, and services necessary to execute and complete the works in accordance with the approved technical drawings and tender specifications. General Specifications Double-Leaf Access Gate Provision of one double-leaf steel gate fabricated as follows: As per approved drawingss • Main frame: 2 inchs angle bar 5 mm thickness and one inch steel angle, Footing depth: 80 cm minimum, Footing dimensions: As per approved drawingss) • Fitted with: • Four (4) heavy-duty hinges Drop bolts with holders • Lock provision with padlock 93-95 mm • All necessary accessories for smooth and secure operation Finishing • All steel components shall be: • Cleaned and prepared, Two coat of primer, Two coats of anti-rust paint, Two coats of approved enamel paint finish All works shall be executed strictly in accordance with the approved drawings AND Site visit, technical specifications, and conditions outlined in the tender documentation. | L.S | 1
C.4 | Backfilling using selected materials inside the WTP perimeter Fence using approved selected fill material, the fill shall be placed in uniform layers not exceeding 200 mm in thickness and compacted mechanically. The work shall include site preparation, hauling, spreading, moisture conditioning, compaction, trimming to the required levels and slopes.as follows: • Southern side (south of filters) = 30.0m (length)x 6.0m width x 1.0m depth. • Northern side (North of filters) = 50.0m (length)x 6.0m width x 0.5m depth. | M3 | 330
C.5 | Control Room (external dimensions: 3.6x3.6m): Backfilling around south-eastern side of the building. Casting lean concrete aprons around the room perimeter. Prepare and apply internal painting for walls using three coats of high-quality PVA emulsion (Bomastic), including surface preparation using SBR and Grout for cracks fixing , , and final finishing. Prepare and apply three coats of high-quality exterior acrylic weather-resistant paint to external textured walls, including surface preparation, cleaning, crack filling where required, priming, and final finishing, complete. Repair all external wall and internal cracks using SBR-modified cement grout. Repair damaged walls. Repair and prepare and paint all doors and windows. Repair and restoration of all lighting fixtures to ensure adequate illumination, and installation of proper protection panel for lighting units replacement of broken glass panels with fiber sheets as well as replacing the zinc roof; repair and proper arrangement of electrical connections, renovation and fixing of cable trunking. In addition, removal of unused equipment and materials from inside the pump house shall be carried out in coordination with SWC and relocation outside the pumping house. | LS | 1
C.6 | Guard Room: Prepare and apply internal painting for walls using three coats of high-quality PVA emulsion (Bomastic), including surface preparation using SBR and Grout for cracs fixing , and final finishing. Prepare and apply three coats of high-quality exterior acrylic weather-resistant paint to external textured walls, including surface preparation, cleaning, crack filling where required, priming, and final finishing, complete. Repair all external wall and internal cracks using SBR-modified cement grout. Repair damaged walls. Repair and prepare and paint all doors and windows. Dismantle old seps construct and install new concrete steps to the entrance of the room. Repair and restore all lighting fixtures to ensure adequate illumination. Replace broken glass panels with fiber sheets where required. Repair the zinc roof, apply one coat of anti-rust primer, and finish with the required paint coats. Repair and organize all electrical wiring and connections, and provide four power sockets and one 80 W ceiling fan complete with all required accessories. Supply and install one water dispenser with refrigerator and two water drums, two metal benches (three seats each), and two factory-manufactured powder-coated steel single beds (900 × 2000 mm), each complete with a high-density mattress. Locally fabricated/workshop-made bed frames shall not be accepted. | LS | 1
D | Sedimentation Tanks, Slow Sand Filters, and Clean Water Tanks Rehabilitation
D.1 | Sedimentation Tanks – Two Tanks Approximate tank dimensions: 14.6 m (W) × 28.8 m (L) × 3.5 m depth from the top of the wall to the inlet level. The work shall include the complete cleaning and rehabilitation of the two existing sedimentation tanks, including: Dewater the tanks by pumping out the existing water. Remove all accumulated silt, sludge, waste, vegetation, and biological growth, and transport the removed materials to an approved disposal site. Thoroughly clean the internal surfaces of the tanks to restore proper hydraulic and treatment performance. Inspect the tank structure and repair any cracks found using suitable epoxy or polyurethane crack-injection materials. Clean the tanks after completion and safely dispose of all waste and removed materials in coordination with the relevant authorities. Carry out final inspection, testing, and commissioning of the tanks before returning them to service. The price shall include all materials, labor, equipment, dewatering, transportation, disposal, safety measures, and all other works required to complete the rehabilitation and return the tanks to normal operation. | L.S | 1
D.2 | Slow Sand Filters – Two Units Approximate dimensions of each filter: 19.0 m (W) × 37.5 m (L) The works shall include the complete rehabilitation of the two existing slow sand filter units, including: Dewater the filters by pumping out the existing water. Carefully remove and dispose of the existing filter sand, gravel, and underdrain materials at an approved disposal site. Clean the internal surfaces using suitable tools and grinding equipment to remove rust, sediment, and loose materials, and repair/seal any cracks found. Supply and place clean filter sand, free from clay, silt, and organic matter, to a depth of 1.0 m, with: Effective size (D10): 0.15–0.30 mm Uniformity coefficient (Cu): less than 3 Supply and place 0.35 m thick gravel support layer, divided into three properly graded layers: fine, medium, and coarse gravel. Supply and install new perforated underdrain pipes, including all necessary fittings and connections. Carefully level and grade the filter media to ensure a uniform filter bed and proper operation. Clean the filter units after completion and remove all waste and surplus materials from the site. Carry out final inspection, testing, and commissioning of the two slow sand filters. The price shall include all materials, labor, tools, equipment, dewatering, removal and disposal of old materials, supply and placement of new filter media, underdrain replacement, cleaning, testing, and all other works required to return the filters to proper operating condition. | L.S | 1
D.3 | Clean Water Ground Tank – Cleaning and Rehabilitation Approximate tank dimensions: 4.7 m (W) × 24.4 m (L) × 3.0 m water depth. The works shall include the complete cleaning and reinstatement of the existing clean water ground tank, including: Dewater the tank by pumping out the existing water. Remove all accumulated sludge, silt, waste, vegetation, and biological growth from the tank. Carry out manual and/or mechanical desilting, including collection, lifting, loading, and transportation of removed materials. Thoroughly clean all internal surfaces, including the tank floor, walls, inlet/outlet areas, and other associated appurtenances. Safely transport and dispose of all removed materials at an approved disposal site in coordination with the relevant local authorities. Inspect the tank and carry out structural repair works required to restore it to a serviceable condition. Complete final cleaning, inspection, and reinstatement of the tank to service to the satisfaction of the Engineer. The price shall include all labor, equipment, dewatering, cleaning, handling, transportation, disposal, safety measures, and all other works necessary to complete the cleaning and return the tank to normal service. | L.S | 1
D.4 | Supply, install, test, and commission one DN500 (20-inch) wafer-type butterfly valve to replace the existing defective valve. Valve specifications: Type: Wafer butterfly valve Size: DN500 (20") Rating: PN16 Flange compatibility: PN16, and ANSI Class 150 Body: Min of Ductile cast iron GGG50 Disc: Stainless steel 1.4408 Seat: FPM/FKM (Viton) Face-to-face: EN 558-1, Series 20 Operation: Manual gearbox with handwheel The works include removing the existing valve and handing it over to SWC, then supplying and installing the new valve. This includes proper alignment, gaskets, bolts, seals, and all necessary fittings. Where needed, a dismantling joint or flanged pipe of the same diameter shall be provided to ensure proper installation and future maintenance of the valve. The installed valve shall be pressure and leakage tested, checked for proper operation, and commissioned to the satisfaction of the Engineer. The price shall include all labor, materials, tools, equipment, and accessories needed to complete the work. | No. | 4
D.5 | Chamber construction and concrete works: Construction of valve chamber using Fired red bricks first class block masonry, in accordance with approved drawings and specifications, suitable for 500 mm control valve , minimum internal dimensions 1.50 m × 1.50 m × 1.20 m. Includes excavation, disposal, backfilling and compaction; reinforced concrete works; block masonry; internal and external plastering; drainage provisions; access steps; waterstop installation or flexible sealant boots/styrofoam at wall penetrations; finishing works. Chamber fitted with galvanized steel chequered plate cover (thickness 3mm) with lockable hinges, complete and operational. Rate to include all labour, materials, equipment, and incidentals, complying with applicable international standards and UN technical requirements. | No. | 4
D.6 | Supply and installation of sludge pumps with new submersible slurry/sewage units, including all complete with power cables, discharge hoses (20 m), lifting chains, and any required accessories, and commissioning. Each pump shall meet the following requirements: Flow rate (Q): minimum 50 m³/h Total head (H): 15–18 m Power: 5.5 kW Operating voltage: 380 V Materials and construction: Pump casing: GG20/GG25 Impeller: CF8M (316 Stainless Steel) Pump shaft: Stainless Steel All components shall comply with the technical specifications and ensure reliable and efficient operation of the sludge pumping system. | No. | 2
D.7 | Supply, install, test, and commission one electromagnetic diaphragm chlorine dosing pump equivalent to Lutz-Jesco MAGDOS LB 6, with a dosing capacity of 6.3 L/h at 4 bar (6.2 L/h at 8 bar), operating on 100–240 V AC, 50/60 Hz, with a power consumption of 28 W and enclosure protection IP65. The pump shall be suitable for sodium hypochlorite dosing and supplied complete with mounting bracket, foot valve with strainer, injection valve, suction and discharge tubing, electrical cable, and all accessories required for a complete operational system. | No. | 2
E | DN300 carbon steel discharge header complete with welding, flanged connections, alignment, and supports
E.1 | Rehabilitation of the leaking 12-inch valve through mechanical repair works to eliminate leakage and restore full operational condition. The works shall include inspection, tightening/replacement of internal seals and worn components as necessary. The scope also includes renovation of the valve chamber, comprising repair of damaged surfaces, re-plastering with cement-sand mortar using a mix ratio of 1:8, and repainting of the chamber cover with approved protective paint. | LS | 1
E.2 | Dismantling, removal, and safe disposal off-site of the existing discharge header system from pumps to the valve end, including all pipes (steel/RC embedded sections), buried and wall-embedded parts (sleeves, anchors, and cast-in components), fittings, supports, valves, bolts, and associated accessories. Works shall include cutting, lifting, handling, and removal without damaging adjacent structures, and reinstatement of affected areas where required. | LS | 1
E.3 | Supply, fabricate, and install DN300 (12”) carbon steel main header pipe, ASTM A53 Grade B, Schedule 40 (323.9 × 10.31 mm), complete with cutting, welding, alignment, supports, and installation, including connection to existing DN300 (12”) gate valve via PN16 flanged joint, total manifold length 5 m, and including excavation, sand bedding, backfilling, compaction, and all necessary fittings, consumables, and accessories for a complete and proper installation and commissioning. | ml | 15
E.4 | Supply, fabricate and install branch pipes: DN200 (8") for the three Pumps, carbon steel ASTM A53 Grade B Sch 40, complete with welding and fittings. 1.2 m for each pump | m | 3.6
E.5 | Supply and install PN16 12 holes weld neck flanges Stainless Steel (304 / 316) DN200 Including rubeer gaskets and stainless steel bolts size M24, nuts, washers, and alignment. | No. | 6
E.6 | Supply and install PN16 12 holes weld neck flanges Stainless Steel (304 / 316) DN300 Including rubeer gaskets and stainless steel bolts size M24, nuts, washers, and alignment. | No. | 2
E.7 | Supply and install DN300 PN16 dismantling joint flanged, installed immediately downstream of the connection to the existing 12" (DN300) gate valve and between the puddle flange and DN300 equal flanged tee. Including rubeer gaskets and stainless steel bolts size M24, nuts, washers, and alignment. | No. | 2
E.8 | Supply and install DN300 × DN300 × DN300 equal flanged tee, PN16, ductile iron to EN 1092-2, internally and externally epoxy powder coated overall face-to-face length approximately 800 mm, with integrally cast flanges, rubber gaskets, and stainless-steel bolting, complete with installation and hydrostatic testing. | No. | 1
E.9 | Supply and install DN300 × DN300 × DN200 reducing flanged tee, PN16, ductile iron to EN 1092-2, internally and externally epoxy powder coated overall face-to-face length approximately 800 mm, with integrally cast flanges, rubber gaskets, and stainless-steel bolting, complete with installation and hydrostatic testing. | No. | 3
E.10 | Supply and install Stainless blind flangesDN 300 EN1092-1, PN16, end caps ncluding rubber gaskets and stainless steel bolts size M24, nuts, washers, and alignment. and all fittings required to complete the header. | No. | 2
E.11 | Supply and construct C30/37 reinforced-concrete pipe supports complete with fabricated carbon-steel saddles for the DN300 main header and DN200 pump branches. The supports shall be provided at eight (8) locations: S-1: Approximately 300 mm from the left DN300 blind flange. S-2: Adjacent to the DN300 × DN300 equal tee. S-3: Between the right-side DN200 branch connections. S-4: Approximately 300 mm from the right DN300 blind flange. S-5: Between the DN300 × DN300 equal tee and DN300 × DN200 reducing tee. S-6 to S-8: At the three DN200 pump branch connections. RC supports: S-1 to S-5: min of 600 × 600 × 500 mm for DN300 pipe. S-6 to S-8: min of 500 × 500 × 450 mm for DN200 pipe. Concrete: C30/37 minimum. Reinforcement: high-yield steel, with spacing and arrangement as per drawing and approved by the Engineer. Minimum concrete cover: 50 mm. Supports shall be properly founded or securely anchored adhsive to the existing concrete slab where the existing structure is confirmed adequate. Metallic saddles: For DN300 pipe: Pipe outside diameter: 323.9 mm. Saddle material: ASTM A36 or S275 carbon steel. Saddle plate thickness: 10 mm minimum. Saddle width: 200 mm minimum. Bearing angle: approximately 120° (60° each side). Provide 10 mm neoprene/rubber liner between the saddle and pipe. Provide stiffeners and suitable anchor bolts as required. For DN200 pipe: Pipe outside diameter: 219.1 mm. Saddle material: ASTM A36 or S275 carbon steel. Saddle plate thickness: 10 mm minimum. Saddle width: 150 mm minimum. Bearing angle: approximately 120° (60° each side). Provide 10 mm neoprene/rubber liner between the saddle and pipe. Provide stiffeners and suitable anchor bolts as required. Steel saddles shall be protected with zinc-rich primer and epoxy/polyurethane coating. Saddles shall be accurately positioned, leveled, and aligned and shall not restrict required pipe movement. Where supports are fixed to an existing concrete slab, drilling and chemical/mechanical anchoring shall only be carried out after confirming the condition and thickness of the existing concrete. The price shall include C30/37 concrete, reinforcement, formwork, foundations/anchoring, steel saddles, stiffeners, anchor bolts, rubber/neoprene liners, protective coating, installation, alignment, curing, and all necessary materials and labor. | LS | 1
E.12 | Supply and install DN300 (12") steel puddle flange fabricated from carbon steel pipe, ASTM A53 Grade B / ASTM A106 Grade B, Sch 40 (minimum 10 mm thickness), complete with welded flange plate, designed for embedding into reinforced concrete walls or structures to provide a watertight seal for pipe penetration. | No. | 1
E.13 | Internal lining of all carbon steel header pipes shall be provided with a potable water approved epoxy coating in accordance with AWWA C210 or equivalent EN/ISO standard/ SWC standards suitable for drinking water applications. Surface preparation to a minimum standard with ISO 8501-1. External protection for all buried or underground steel pipe sections shall be provided using an approved anti-corrosion coating system suitable for soil burial conditions, complying with ISO 12944 and/or equivalent EN standards, consisting of primer, intermediate, and finish protective layers. All coating works shall include inspection. | LS | 1
E.14 | Provide necessary equipment for Hydrostatic pressure testing of complete system at 1.5 × working pressure including flushing and cleaning, Commissioning and handover of complete pumping header system. | LS | 1
F | Pump House Rehabilitation
F.1 | Rehabilitation of old pump house (external dimensions: 9.6x4.6m); including dismantling of existing Zinc sheets and installing new ones. The works include (3) skylights (2 on the north and 1 on the south) securing,painting and repairing windows and doors. Prepare and apply three coats of high-quality exterior acrylic weather-resistant paint to external textured walls, including surface preparation, cleaning, crack filling where required, priming, and final finishing, complete; Repair all external wall and internal cracks using SBR-modified cement grout. Cleaning and rehabilitation of the WTP pump house, including general cleaning of walls, floors, and columns, and removal of grease, dust, and accumulated dirt. Prepare and apply internal painting for walls using three coats of high-quality PVA emulsion (Bomastic with paint final color), including surface preparation using SBR and Grout for cracks fixing , sanding, and final finishing. Repair and restoration of all lighting fixtures to ensure adequate illumination, and installation of proper protection panel for lighting units. The scope shall also include painting the metallic pipes in the WTP, repair and proper arrangement of electrical connections, renovation and fixing of cable trunking, and application of new paint to internal surfaces after cleaning and surface preparation. In addition, removal of unused equipment and materials from inside the pump house shall be carried out in coordination with SWC and relocation outside the pumping house. | L.S | 1
F .2 | Construction of a new pump house extension with internal dimensions of 9.0 m × 4.0 m, including all materials, labour, equipment, and associated works required for completion in accordance with the approved drawings and specifications. 1. Site Preparation and Foundation Works • Clear the site • Excavate strip foundations along the room perimeter, approximately 400 mm × 300 mm deep, total length (17.5 m). • Provide 300 mm thick granite stone pitching laid in 1:8 cement-sand mortar. • Construct a 400 mm wide and 300 mm deep brick foundation below the grade beam using first-class fired bricks and 1:6 cement-sand mortar. (17 M) • Construct reinforced concrete grade beam, 300 × 300 mm, using 1:2:4 concrete, reinforced with 4 No. 12 mm steel bars and 8 mm stirrups at 200 mm c/c.: (1.6 m³). • Backfill with approved selected material and compact in layers to a final mechanical compacted thickness of 450 mm. (21 M3) • Construct reinforced concrete floor slab on prepared and compacted ground, 150 mm thick, using 1:2:4 concrete and 12 mm reinforcement at 200 mm c/c, including leveling, finishing, curing, propre drainage, and all associated works. (5.3 M3) 2. Superstructure • Construct walls up to 1.0 m height, including parapet, using first-class fired bricks and 1:6 cement-sand mortar. Include watering and curing for a minimum of 3 days. Approximate wall area: (17 m²). • Properly connect the new structure to the existing pump house. The new reinforced concrete beam shall be dowelled and tied to the existing beam/wall using 12 mm diameter reinforcement bars with approved chemical anchors . • Provide internal and external steel angle supports across the joint, securely fixed using M14 Fischer expansion anchor bolts. Include all drilling, cutting, anchoring, welding, fixing, and finishing required for a complete connection. 3. Steel Structure and Cladding • Supply, fabricate, and erect the pump shed steel frame using RHS 80 × 40 × 2 mm sections, including 9 posts, approximately 2.8 m high, securely embedded and fixed to the grade beam. • Provide galvanized welded wire mesh panels of approximately 6 × 3 mm wire/mesh size with 1 mm thickness, including supporting frames and bracing, attached with Green Power Mesh Fabric. (At 1 m height ) • Provide zinc sheet cladding above the mesh section, including steel framing, bracing, fixing accessories, and all necessary works. (At 0.8 hight) 4. Doors and Windows • Supply, fabricate, and install one double-leaf steel door, 1.20 × 2.20 m, using RHS sections, including 80 × 40 × 1 mm main frame, 60 × 30 × 1 mm leaf frame, and 15 mm× 15 mm internal framing, complete with fittings. • Supply, fabricate, and install four double-leaf steel windows, 1.00 × 1.20 m, using 60 × 30 × 1 mm RHS frames, 40 × 20 mm leaf frames, and 15 mm× 15 mm internal framing, complete with fittings.. 5. Roofing • Construct three (3) galvanized steel gable roof trusses across the short span using 80 × 40 × 2 mm RHS steel sections. • Provide and install the longitudinal horizontal roof members using 80 × 40 × 2 mm RHS steel sections, spaced at 800 mm c/c and securely connected to the roof trusses. • Supply and install 0.5 mm minimum thickness corrugated galvanized zinc roofing sheets, securely fixed using suitable J-bolts with rubber washers to ensure a watertight installation. • Connect and securely fix the new roof structure to the existing pump house roof structure, including all required brackets, welding, bolts, and connection accessories. • Include adequate overlaps, flashing, sealing, fasteners, and all accessories required for a complete and weather-tight roof. • All steel members shall be cleaned and protected with anti-rust coating followed by two coats of approved oil-based paint. • Total roofing area: 40.5 m². 6. Plastering and Painting • Apply cement-sand plaster in 1:6 mortar to walls, including surface preparation, leveling, finishing, and curing. (34 m².) 7. Electrical and Other Works • Supply and install two Orient ceiling fans 80 w, complete with anchor wiring 1.5 mm² cable wiring, brackets, switches, testing, and commissioning. • Supply and install six LED lights, minimum 56 W each, including 1.5 mm² cable wiring, fittings, accessories, testing, and commissioning. • Construct concrete entrance steps, including excavation, formwork, concrete, finishing, and all associated work. • Seal and repair all existing wall penetrations and openings in the pump house. • Rainwater will be collected through roof gutters and directed through 4-inch PVC drainage pipes. The pipes will be discharged on the southern side of the pump house and extend approximately 15 m away from the building to prevent water from accumulating around the foundation. The system will be installed with a suitable slope for free drainage and will include all necessary fittings, supports, connections, and accessories. The drainage system will also collect, and discharge water generated inside the pump house. • Provide new wall penetrations for the suction pipes of the three pumps, including sleeves, sealing, finishing, and all necessary accessories. | Job | 1
F.3 | Dismantle the existing pump and hand it over to SWC outside the pump house. Supply, installation, testing, and commissioning of a heavy-duty horizontal split-case double suction centrifugal pump for raw water application, complete with electric motor, base frame, coupling- wool coupling with a band width of less than 10 cm, coupling guard, and accessories, no new pipe supply is included, fusion welding for the piping system. Detailed Specifications: Duty Point: Q = 300 m³/h, H = 70 m. Mounting: Supply, cast, and cure a reinforced concrete foundation of minimum C25/30 concrete. Foundation dimensions shall be based on the pump manufacturer's certified foundation drawing, with sufficient projection beyond the base frame on all sides. Foundation thickness shall be approximately 400 mm, or as required to align the pump suction centerline with the existing suction pipeline. Anchor bolts, sleeves, non-shrink grout, leveling, and alignment shall be included. Type: Horizontal Split Case, Double Suction Centrifugal Pump Impeller: Closed, dynamically balanced. Speed: Approximately 2950 RPM at 50 Hz. Minimum Pump Efficiency: Not less than 80% at the specified duty point. Materials of Construction: • Casing: Cast Iron EN, internally coated with epoxy coating, minimum 200 microns DFT; Impeller: Stainless Steel ASTM (AISI 316 equivalent); Shaft: Stainless Steel AISI or equivalent conforming to ASTM A276; Shaft Seal: Gland Packing (soft packing suitable for raw/silt-laden water). Pipe at the Suction Line: Existing HDPE PE100 SDR17 PN10 pipeline, DN250, The pipe already exists; pricing shall cover only the hookup pipe supports, removable flanged spool pieces, flanges, backing rings/adaptors, gaskets, fasteners, and fittings required for pump installation and future removal. Fittings at Suction Line: Flanged full-bore Foot Valve, Ductile Iron body with integral Stainless-Steel strainer, DN250 PN10; flanged eccentric reducer (flat side up) from DN250 to the pump suction flange; 90-degree long-radius elbows, pressure-rated fittings compatible with the piping system. Pipe at the Discharge Line: Existing HDPE PE100 SDR17 PN10 pipeline, DN200, conforming to ISO 4427. The pipe already exists; pricing shall cover only the hookup pipe supports, removable flanged spool pieces, flanges, backing rings/adaptors, gaskets, fasteners, and fittings. Fittings at Discharge Line: Flanged concentric reducer pn 16; 90-degree long-radius elbows, pressure-rated fittings compatible with the piping system, valve and NRV DN 200 PN 16 with all accessories Motor Power: 90 kW; Motor Speed: Approximately 2950 RPM at 50 Hz. Motor Specifications: Type: Three-phase Squirrel Cage Induction Motor; Cooling: TEFC (Totally Enclosed Fan Cooled); Protection Class: IP55. Scope of Supply: Supply, install, align, test, and commission a complete pump unit on base frame for, including TEFC motor, flexible coupling with coupling guard, suction and discharge hookup piping with fittings, removable flanged spool pieces, pipe supports (as determined on site), flanges, backing rings/adaptors, gaskets, fasteners, and all accessories necessary for a complete installation. Suction and discharge pipework shall be independently supported so that no external loads are transmitted to the pump flanges. Pumps and control boxes shall be clearly labeled. The tenderer shall submit certified pump performance curves, including Head vs. Flow, Efficiency, Brake Power, and NPSH Required at 300 m³/h, and shall verify that the selected pump satisfies the specified duty point considering all pipeline and fitting losses. (More details on the site visit.) | No. | 1
F.4 | Dismantle the existing pump and hand it over to SWC outside the pump house. Supply, installation, testing, and commissioning of a heavy-duty horizontal split-case double suction centrifugal pump for raw water application, complete with, base frame, coupling -wool coupling with a band width of less than 10 cm, coupling guard, and accessories. (The motor already exists with 90 kw power), no new pipe supply is included, fusion welding for the piping system. Detailed Specifications: Duty Point: Q = 300 m³/h, H = 70 m. Mounting: Supply, cast, and cure a reinforced concrete foundation of minimum C25/30 concrete. Foundation dimensions shall be based on the pump manufacturer's certified foundation drawing, with sufficient projection beyond the base frame on all sides. Foundation thickness shall be approximately 400 mm, or as required to align the pump suction centerline with the existing suction pipeline. Anchor bolts, sleeves, non-shrink grout, leveling, and alignment shall be included. Type: Horizontal Split Case, Double Suction Centrifugal Pump Impeller: Closed, dynamically balanced. Speed: Approximately 2950 RPM at 50 Hz. Minimum Pump Efficiency: Not less than 80% at the specified duty point. Materials of Construction: • Casing: Cast Iron EN, internally coated with epoxy coating, minimum 200 microns DFT; Impeller: Stainless Steel ASTM (AISI 316 equivalent); Shaft: Stainless Steel AISI or equivalent conforming to ASTM A276; Shaft Seal: Gland Packing (soft packing suitable for raw/silt-laden water). Pipe at the Suction Line: Existing HDPE PE100 SDR17 PN10 pipeline, DN250, The pipe already exists; pricing shall cover only the hookup pipe supports, removable flanged spool pieces, flanges, backing rings/adaptors, gaskets, fasteners, and fittings required for pump installation and future removal. Fittings at Suction Line: Flanged full-bore Foot Valve, Ductile Iron body with integral Stainless-Steel strainer, DN250 PN10; flanged eccentric reducer (flat side up) from DN250 to the pump suction flange; 90-degree long-radius elbows, pressure-rated fittings compatible with the piping system. Pipe at the Discharge Line: Existing HDPE PE100 SDR17 PN10 pipeline, DN200, conforming to ISO 4427. The pipe already exists; pricing shall cover only the hookup pipe supports, removable flanged spool pieces, flanges, backing rings/adaptors, gaskets, fasteners, and fittings. Fittings at Discharge Line: Flanged concentric reducer pn 16; 90-degree long-radius elbows, pressure-rated fittings compatible with the piping system, and NRV DN 200 PN 16 with all accessories Scope of Supply: Supply, install, align, test, and commission a complete pump unit on base frame for, including TEFC motor, flexible coupling with coupling guard, suction and discharge hookup piping with fittings, removable flanged spool pieces, pipe supports (as determined on site), flanges, backing rings/adaptors, gaskets, fasteners, and all accessories necessary for a complete installation. Suction and discharge pipework shall be independently supported so that no external loads are transmitted to the pump flanges. Pumps and control boxes shall be clearly labeled. The tenderer shall submit certified pump performance curves, including Head vs. Flow, Efficiency, Brake Power, and NPSH Required at 300 m³/h, and shall verify that the selected pump satisfies the specified duty point considering all pipeline and fitting losses. (More details on the site visit.) | No. | 1
F.5 | Complete rehabilitation of the existing pump, motor, coupling, control box and electrical connections, including repair/replacement of defective components this Including fabrication of a new pump shaft from suitable high-strength stainless steel approved material, accurately machined to the required dimensions, including keyways, threads, fits, balancing, and all necessary machining and finishing works, alignment and servicing. Disconnect, transfer and reinstall the complete pump unit at the new pump house, including flexible coupling and coupling guard. The work shall include the supply and installation of an approved straight-through joint kit for connecting the existing power cables, complete with suitable connectors, heat-shrink/cold-shrink insulation and moisture sealing, including testing of the completed cable joint. Provide and construct a minimum C25/30 reinforced-concrete foundation, approximately 400 mm thick or as required, based on the pump manufacturer's foundation and alignment requirements, including anchor bolts, leveling and non-shrink grout. Pipe at the Suction Line: Existing HDPE PE100 SDR17 PN10 pipeline, DN250, The pipe already exists; pricing shall cover only the hookup pipe supports, removable flanged spool pieces, flanges, backing rings/adaptors, gaskets, fasteners, and fittings required for pump installation and future removal. Fittings at Suction Line: Flanged full-bore Foot Valve, Ductile Iron body with integral Stainless-Steel strainer, DN250 PN10; flanged eccentric reducer (flat side up) from DN250 to the pump suction flange; 90-degree long-radius elbows, pressure-rated fittings compatible with the piping system. Pipe at the Discharge Line: Existing HDPE PE100 SDR17 PN10 pipeline, DN200, conforming to ISO 4427. The pipe already exists; pricing shall cover only the hookup pipe supports, removable flanged spool pieces, flanges, backing rings/adaptors, gaskets, fasteners, and fittings. Fittings at Discharge Line: Flanged concentric reducer pn 16; 90-degree long-radius elbows, pressure-rated fittings compatible with the piping system, valve and NRV DN 200 PN 16 with all accessories Complete the installation with independent pipe supports, pump and control-box labeling, mechanical and electrical testing, alignment, leak testing, trial operation and commissioning. Suction and discharge pipework shall be independently supported. The pump and control box shall be clearly and permanently labeled. All necessary materials, fittings, accessories, labour, lifting/transfer and site works shall be included. (Further details on the site visit.) | No. | 1
F.6 | Supply, installation, testing, and commissioning of an IP54 wall-mounted star–delta starter control panel with interlock between star and delta contactors suitable for a 90 kW, 415 V, 3-phase pump motor, complete with a 250 A, 3P MCCB main isolator; AC-3 rated contactors including 225 A main, 125 A delta, and 95 A star contactors; adjustable star–delta timer; thermal overload relay (160-200 A range) and set in accordance with the motor manufacturer's nameplate full-load current.and installed in the main line; control circuit components including 6–10 A, 1P MCB, 220–240 V control voltage system, phase failure relay, auxiliary relays, push buttons (Star, Stop, and emergency stop), and selector switches; indication lamps for Power ON, Star, Delta, Trip status, and Analog Ameter and voltmeter; and a steel enclosure with IP54 minimum protection mounted using M14 expansion anchors( Fischer screws) or approved equivalent. The scope also includes complete internal wiring, ferruling, labeling, terminal blocks, cable glanding and termination to the motor and power source using appropriate cable lugs, on-site testing and commissioning, and provision of all necessary accessories and minor materials required to deliver a fully functional and operational system. Motor technical data: 90 kW, 415 V ±10%, 50 Hz, 3-phase; The star–delta control panel shall be connected to the power supply using the two of 4C 35 mm² cables; ensuring proper termination with suitable cable lugs, glands, and secure connections. The installation shall include verification of cable condition and capacity, proper phase identification, and adequate tightening, with provision of all necessary accessories and materials. | No. | 2
F.7 | Supply and install of reinforced copper cable, 3.5C × 35 mm² XLPE/SWA/PVC power cable, 0.6/1 kV, including cable laying on tray and routing to ground level, proper termination with lugs, dressing and connection to the motor, gland installation at the control panel and hings, and complete connection to the control panel, all in accordance with project specifications, this is for the new pumps inside the WTP. | ML | 140
F.8 | Supply, install, test, and commission one Pentax CM centrifugal pump (or approved equivalent), capacity 150 L/min at 35 m head, single-phase 220 V, 50 Hz, complete with 16 A 2-pole MCB, voltage/current protector, control box, and 4 mm² copper cable installed in PVC trunking; provide fixed 2-inch PPR suction and discharge pipework, including a 3 m suction line with adequate pipe supports; install a 2-inch brass foot valve with female NPT connection and integrated mesh strainer at the suction end, a 2-inch non-return valve on the discharge line, and a 1-inch branch connection at each pump (three) complete with PPR tee, PPR ball valve union, female socket, brass valve and all required reducers, elbows, adaptors, couplings, and fittings for the priming and return line arrangement between the pump inlet and isolation valve, including all accessories necessary for a complete, tested, and fully operational installation as well as to construct a sheleter for the pump. (More details on the site visit) | LS | 1
G | Safety and Fire Resistance Equipment
G.1 | Supply and installation of trolley-mounted CO₂ (Carbon Dioxide) fire extinguishers, each with a 30 kg capacity, suitable for extinguishing Class B fires and fires involving energized electrical equipment, including all necessary accessories and a robust wheeled trolley. The extinguishers shall be brand new, fully charged, certified, and suitable for energized electrical equipment, with the applicable fire classification and certification clearly marked on each unit. Each unit shall include a suitable discharge hose/horn, safety pin, tamper seal, operating valve and trolley, and shall comply with applicable BS EN 1866-1 or equivalent requirements. The Contractor shall provide basic operational training to the pump operator on the safe and correct use of CO₂ fire extinguishers. Training shall be conducted using a separate extinguisher designated for training purposes and shall not involve discharging the installed units. | No | 2
I | Signboard
I.1 | Supply, fabrication, transportation, and installation of a project signboard comprising four (4) steel panels, each measuring 150 × 30 cm, mounted on a steel frame fabricated from 60 × 30 mm box section steel, 3 mm thick. The signboard panels shall be manufactured from 1.2 mm thick steel sheets, with a clear 80 mm gap between adjacent panels. The panels shall be fixed to steel support legs fabricated from 3-inch (75 MM) DIAMETER Circular steel pipe, 3 mm thick wall thickness, securely anchored into two (2) pits, each measuring 50 × 50 × 50 cm, using plain concrete (1:3:6 mix). The item shall include surface preparation, application of an anti-rust primer, and three coats of oil-based paint, finished with a white background and blue lettering, in accordance with the approved mock-up drawings and the directions of the IOM Engineer. The rate shall include all materials, accessories, labor, tools, equipment, transportation, and complete installation, fully finished and ready for use. | No | 1
TOTAL COST

## Two(2) stances toilet Banat
Bill of Quantities ( BOQ)
Project Name : Sudan Integrated Social Sector Infrastructure Rehabilitation Project (SISSIRP) Project Type : WASH Project Locations: Sennar , Jebal Moya Staff's(2) stances toilet blocK- at Jebal Moya WTP- Banant Alnifdia. Project Duration: days
General Guidelines
1 | Design plans and BoQ are complementary to each other, hence the contractor has the obligation to execute the tasks mentioned in either one of them. Accordingly The contractor's shall include all what is mentioned in the drawings & all what is mentioned in the BOQs. Incase BOQ and technical drawings have discrepancies. BOQ supersedes technical drawings. Follow IOM site engineers site instruction at all times.
2 | All the BoQ articles comprise supplying manpower, machinery, equipment, transportation all necessary requirements to get the work done properly regardless of it's mentioned in the BoQ articles or not.
3 | In case that there is any item or detail in the drawings not mentioned in the BOQ (or vise versa) then this item or detail is considered included in the contractor's price for this project & he should execute it within his contract price without claiming any increase to the contract price, as it is considered part of the contract.
4 | All the BoQ articles must be carried out according to the guidelines of Sudanese Technical Specifications, with updates and instructions of IOM Engineer.
5 | All the BoQ articles comprise removing and transporting any debris or rubble to allocated disposal areas by municipality or local authority.
6 | The Contractor must obtain prior written approval from the IOM Programme Manager and the Procurement Unit for any cost-related Variation Orders. IOM Engineer will record and justify any variations to both parties. No VO shall be implemented without the Programme Manager's written approval.
7 | Site visit is required for vendor to see / inspect project, and to submit a letter mentioning site been visited with tendering documents.
8 | Follow IOM Engineer's instruction at all times.
9 | Submit work plan schedule for project activities.
Technical Specifications:
1 | The price includes all required materials, fittings , accessories , tools , machines , instruments, labor works with all the requirements, installing , testing and commissioning and put in operation to get the system work properly as per international specifications , beneficiary and IOM engineer instructions and to complete the works as stated in the contract items , shop drawings , details and complete the work in all aspects.
2 | Supplying of materials shall not be done before getting IOM Engineer's approval on the materials type, also the contractor should provide certificate of origin and tests result certificate for the supplied materials
3 | All materials should be a good quality and the brand and origin should be subject to the approval of IOM Engineer . Show sample for IOM Engineer's approval before installing. Cost include transportation and installation. Follow IOM Engineer's instruction during installation.
4 | Any damaged parts in any system or structure due to the work in the site , will be responsibility of contractor to redo poor workmanship without cost to IOM .
5 | Contractor / vendor is responsible to delivered all the works to local authority,beneficiary as well as IOM Engineer.
6 | Curing for all concrete works should be maintaied 24 hours, the curing should be not less than 7 days before construction start above any concrete structure
7 | Cleaning the site from any debris during and after complete all the work.
8 | The Contractor shall equip all materials, workers and equipment necessary for the performance of the work specified in the Bill of Quantities and Drowings in all its aspects.
9 | All Electrical connection shall be tested and commissioned before handover to IOM Engineer
10 | The company will be responsible for getting all approval documents from the government authorities in the State
11 | All the fees for materials transport handling and testing of samples should be paid by the Contractor if it mentioned in the BoQ or not.
12 | The Contractor implementing this project should hire laborers and workers from the Locality as much as possible.
# | Description of Work | Unit | Quantity | Unit Rate USD | Amount USD | Remarks
1 | General
A | Mobilization and Demobilization
A.1 | Mobilization and demobilization of vehicles, tools, materials and personnel required for the works, including transport of technical and administrative teams to site. Works include site preparation—leveling, backfilling, and grading—and provision of temporary facilities such as shelters, water supply, and HSE amenities. All activities shall be carried out under qualified engineering supervision using approved materials in accordance with standard specifications. | L.S | 1
2 | Two(2) stances toilet block
B | Substructure
B.1 | Excavation of a pit with internal dimensions of 4.7m*2.7m*2.5m depth (Septick tank). The bottom of the excavation must be trimmed, leveled and compacted to receive the base layer, and the Contractor must adhere to all safety regulations and local standards throughout the work. all suitable excavated materials shall be used to form backfilling with proper compaction. | m3 | 32
B.2 | Supply materials and cast a plain concrete with a thickness of 10 cm(1:3:6) on the prepared and approved subgrade. | m2 | 12.7
B.3 | Provide & Cast Reinforced Concrete 1:2:4 floor slab for septic with 20 cm thickness reinforced with 12mm bars 15cm c/cin both directions (top and bottom layer). Rates to include for form work, workmanship and curing as directed by the engineer . Concrete shall be mechanically mixed, placed and vibrated. | m3 | 2.54
B.4 | Supply and Construction of 1/2 brick shuttering Wall (two sides of RC wall) with cement sand mortar1:6 : includes, using approved bricks and cement sand mortar, complete with alignment, bonding, curing, and all necessary workmanship as per drawings. rate Inclusive divided walls | m2 | 30
B.5 | supply materials and cast R.C(mix1:2:4) side walls with T12 @15cm c/c (Horizontal & vertical)thickness15cm. Rates include form work, workmanship and curing for7 days min. as directed by theengineer. | m3 | 6
B.5 | Supply and apply Plastering of cement-sand(1:6) mortar ,for walls , including surface preparation, mixing, application, leveling, finishing, curing, and all complete as per specifications.The pit lining should extend 50 CM above the ground level. | m2 | 35
B.6 | Supply and implement waterproofing for the pit walls using an approved bituminous flancoat material, provided that the surface is cleaned well from dust and mortar residues, then at least three layers of flancoat are painted, taking into account the overlapping of the layers and the perpendicularity of the direction of the paint, in accordance with the engineer’s instructtions and approved technical specifications. | m2 | 35
B.7 | Supply materials and cast reinforced concrete for cover slab with thickness of 15cm(1:2:4).Reinforcement shall consist of 12 mm diameter steel bars spaced (15cm c/c)apart in both directions (top or bottom layer). Concrete shall be mechanically mixed, placed and vibrated. the rate include (3)inspection opening as per drawings. | m3 | 2
C | Toilet Foundation
C.1 | Strip foundation for the toilet Walls:Excavate Strip Foundation with dimension 50cmx40x70cm depth. | ML | 11
C.2 | Supply materials and Lay stone for strip foundation with granite stone masonry stone using cement sand mortar 1:6 width 40cm, and 50 cm depth as per drawings with best workmanship. | m3 | 3
C.3 | Supply materials and build 2 bricks wall with sand cement mortar 1:6 width 40cm, and 50 cm depth under gradebeam. | ML | 10
C.4 | Backfilling: spupply selected materials and backfill in layers 25cm, watered and compacted to achieve relative density 95%, according to the engineer instructions. | m3 | 7
C.5 | Soak Away Pit: excavate effluent soak- away well with diameter of 2m x 2.5m depth (depends on lowes summer water table), rimmed with burnt clay bricks, header bond(cement: sand) mortar, filled with graded hardcore , covered by a sheet of polyethylene or iron sheet and buried. | LS | 1
D | Sanitary Plubming system
D.1 | Supply , lay and connect PVC waste drainage pipes (PVC 8-inch,6inh, 4inch). The rate inclusive digging trenches, cuttings , threading, joining with all necessary fittings branches , elbows, bends ,tees plugs unions and clips. | LS | 1
D.2 | Provide materials and build one brick wall manholes of sizes (60x60cm and 45x45cm)with invert levels,rate shall include gully trap (30x30) cm. . The rate shall include excavation, backfilling, plastering and provide heavy duty covere for manholes. | LS | 1
E | Superstructure (toilet dimensions 1.7x2.C/C for each)
E.1 | Supply materials and Construction Masonry Walls (one Brick Thick) with Cement Mortar1:6 the rate includes parapet. | m2 | 40
E.2 | Supply and apply an SBR-modified cement mortar screed (1:6 cement:sand mix) to provide the required slope for effective rainwater drainage. SBR bonding agent shall be added at a rate of 2 litres per 50 kg bag of cement, or as recommended by the manufacturer | m3 | 0.5
E.3 | Supply material and cast in situ reinforced concrete tie beam(slab beam) of size 20cm x20cm with 4 Nos. 12 mm bars and stirrups of ø8 mm@ 20cm c/c. Concrete shall be mechanically mixed, placed and vibrated. | ml | 14
E.4 | Provide & Cast Reinforced Concrete 1:2:4 slab for toilet roof with 15 cm thickness reinforced with 12mm bars 15cm c/cin both directions (top and bottom layer). Rates to include for form work, workmanship and curing as directed by the engineer . Concrete shall be mechanically mixed, placed and vibrated. | m3 | 1.2
E.5 | Supply and apply of Cement Plastering includes cement-sand(1:6) mortar ,for walls , including surface preparation, mixing, application, leveling, finishing, curing, and all complete as per specifications. | m2 | 90
E.6 | Supply and apply internal and external painting for walls using three coats of high-quality PVA emulsion (Bomastic), including surface preparation, , sanding, and final finishing. | m2 | 45
E.7 | Supply and apply three coats of high-quality exterior acrylic weather-resistant paint to external textured walls, including surface preparation, cleaning, crack filling where required, priming, and final finishing, complete. | m2 | 45
E.8 | Supply and install walls ceramic tiles size 40 × 40 cm Tile type and quality shall be approved by the engineer based on a submitted sample. Work includes mortar bedding, grouting, leveling, and finishing | m2 | 6
E.9 | Supply materials and install water flush toilet seat(eastern type) complete with cistern and all accessories(Angle valve, shaft, …etc) and necessary fittings, pipe connections. | no. | 2
E.10 | Supply and installation of LED Light at least 56 W complete with lamps, wiring, fixing accessories, testing, and commissioning. | no. | 4
E.11 | Supply and install exhaust fan for bathrooms , each with dimensions 40 cm × 40 cm. The item includes wall opening preparation, mounting, electrical connections, sealing, and testing to ensure proper operation as approved by the engineer. | no. | 2
E.12 | Supply and installation of steel doors fabricated from square steel pipes (8x4 and 6x3), covered with heavy gauge steel sheets, including frames, hinges, locks, painting, and installation of fiberglass skylights (door size 0.8m*2.1m). | no. | 2
E.13 | Supply and install PPR (Hot-Welded) fresh water pipes, 1-inch diameter, extending from the water tank to toilte , The work includes hot welding, installation of fittings such as elbows, tees, unions, couplings, and all necessary accessories. | ml | 20
E.14 | Supply and install fiber glass water tank(vertical) of capacity 500-liter (Tiga brand or equivelant), three-layer, with 1 inch PPR inlet and outlet connections and valves, cover, and accessories as well as all necessary plumbing connections from main WTP line and down to toilets. | no. | 2
E.15 | Construct and install new concrete entrance steps, including excavation, formwork, concrete, finishing, and all associated works, complete. | LS | 1
E.16 | Supply and install a complete shower unit, including shower head, pipework, valves, drainage connection, and all necessary fittings and accessories, complete in all respects. | LS | 1
F | Signboard
F.1 | Project signboard: Supply, fabrication, transportation, and installation of a project signboard measuring 80 × 60 cm, mounted on a steel frame fabricated from 60 × 30 mm box section steel, 3 mm thick. The signboard panels shall be manufactured from 1.2 mm thick steel sheets with a diagonal brace from the same frame box section The panels shall be fixed to Toilet exterior wall, and securely anchored using four Fischer bolts m12 using Cleat angle welded to the frame (1.25 inch) The item shall include surface preparation, application of an anti-rust primer, and three coats of oil-based paint, finished with a white background and blue lettering, in accordance with the approved mock-up drawings and the directions of the IOM Engineer. The rate shall include all materials, accessories, labor, tools, equipment, transportation, and complete installation, fully finished and ready for use. | No | 1
TOTAL COST

## Rehab of Kamar Al-Nayer booster
Bill of Quantities ( BOQ)
Project Name : Sudan Integrated Social Sector Infrastructure Rehabilitation Project (SISSIRP) Project Type : WASH Project Locations: Sennar , Sennar, Rehabilitation of Kamar Al-Nayer booster station Project Duration: days
General Guidelines
1 | Drawings and BoQ are complementary to each other, hence the contractor has the obligation to execute the tasks mentioned in either one of them. Accordingly The contractor's shall include all what is mentioned in the drawings & all what is mentioned in the BOQs. Incase BOQ and technical drawings have discrepancies. BOQ supersedes technical drawings. Follow IOM site engineers site instruction at all times.
2 | All the BoQ articles comprise supplying manpower, machinery, equipment, transportation all necessary requirements to get the work done properly regardless of it's mentioned in the BoQ articles or not.
3 | In case that there is any item or detail in the drawings not mentioned in the BOQ (or vise versa) then this item or detail is considered included in the contractor's price for this project & he should execute it within his contract price without claiming any increase to the contract price, as it is considered part of the contract.
4 | All the BoQ articles must be carried out according to the guidelines of Sudanese Technical Specifications, with updates and instructions of IOM Engineer.
5 | All the BoQ articles comprise removing and transporting any debris or rubble to allocated disposal areas by municipality or local authority.
6 | The Contractor must obtain prior written approval from the IOM Programme Manager and the Procurement Unit for any cost-related Variation Orders. IOM Engineer will record and justify any variations to both parties. No VO shall be implemented without the Programme Manager's written approval.
7 | Site visit is required for vendor to see / inspect project, and to submit a letter mentioning site been visited with tendering documents.
8 | Follow IOM Engineer's instruction at all times.
9 | Submit work plan schedule for project activities.
Technical Specifications:
1 | The price includes all required materials, fittings , accessories , tools , machines , instruments, labor works with all the requirements, installing , testing and commissioning and put in operation to get the system work properly as per international specifications , beneficiary and IOM engineer instructions and to complete the works as stated in the contract items , shop drawings , details and complete the work in all aspects.
2 | Supplying of materials shall not be done before getting IOM Engineer's approval on the materials type, also the contractor should provide certificate of origin and tests result certificate for the supplied materials
3 | All materials should be a good quality and the brand and origin should be subject to the approval of IOM Engineer . Show sample for IOM Engineer's approval before installing. Cost include transportation and installation. Follow IOM Engineer's instruction during installation.
4 | Any damaged parts in any system or structure due to the work in the site , will be responsibility of contractor to redo poor workmanship without cost to IOM .
5 | Contractor / vendor is responsible to delivered all the works to local authority,beneficiary as well as IOM Engineer.
6 | Curing for all concrete works should be maintained 24 hours, the curing should be not less than 7 days before construction start on top any concrete structure
7 | Cleaning the site from any debris during and after complete all the work.
8 | The Contractor shall equip all materials, workers and equipment necessary for the performance of the work specified in the Bill of Quantities and Drowings in all its aspects.
9 | All Electrical connection shall be tested and commissioned before handover to IOM Engineer
10 | The company will be responsible for getting all approval of his documents from the government authorities in the State
11 | All the fees for materials transport handling and testing of samples should be paid by the Contractor if it mentioned in the BoQ or not.
12 | The Contractor implementing this project should hire laborers and workers from the locality as much as possible.
# | Description of Work | Unit | Quantity | Unit Rate USD | Amount USD | Remarks
1 | General
A | Mobilization and Demobilization
A.1 | Mobilization and demobilization of the contractor’s personnel, specialized equipment, tools, lifting devices, transport vehicles, and temporary facilities required for the execution of mechanical, civil, and electrical works under this contract. The item shall include transportation of pumps, motors, installation equipment, welding machines, generators, lifting cranes/chain blocks, testing instruments, and all related tools to and from the project site; establishment of temporary site facilities; provision of supervision and logistics; and final demobilization upon completion of the works. The rate shall also include removal of temporary structures, clearing of the site, and restoration of the work area to its original condition to the satisfaction of the Engineer. | L.S | 1
B | WTP Yard and Fence
B.1 | Construct an embankment, Ground leveling & filling 10 cm yhickness: strpping the topsoil layer, as per engineer's instructions. Level, grade and spread selected filling material (sub-base/ selected soil) in layers not exceeding 20cm watered and compacted to achieve Maximum dry density in accordance to the technical specifications and engineer instructions including Site Clearance emoving of all grass, bushes, shrubs and cutting trees. (to be assessed during site visit). | M2 | 4800
B.2 | Rehabilitate the existing perimeter fence by securing steel angle posts in concrete (40×40×40 cm, 1:3:6 mix), replacing defective posts where required, realigning sections, and tensioning/re-fixing chain-link mesh to restore full fence functionality. All works and quantities to be confirmed on site prior to execution. (to be assessed during site visit). | L.S | 1
B.3 | Construction of a complete Gate including the supply of all materials, labour, tools, equipment, and services necessary to execute and complete the works in accordance with the approved technical drawings and tender specifications. General Specifications Double-Leaf Access Gate Provision of one double-leaf steel gate fabricated as follows: As per approved drawingss • Main frame: 2 inchs angle bar 5 mm thickness and one inch steel angle, Footing depth: 80 cm minimum, Footing dimensions: As per approved drawingss) • Fitted with: • Four (4) heavy-duty hinges Drop bolts with holders • Lock provision with padlock 93-95 mm • All necessary accessories for smooth and secure operation Finishing • All steel components shall be: • Cleaned and prepared, Two coat of primer, Two coats of anti-rust paint, Two coats of approved enamel paint finish All works shall be executed strictly in accordance with the approved drawings AND Site visit, technical specifications, and conditions outlined in the tender documentation. | L.S | 1
C | Construction of Water distribution Point
C.1 | Site clearanceand excavate an area of 4.20 m × 3.20 m × 0.50 m and dispose of all excavated and unsuitable material at an approved disposal site. Rate to include all labour, equipment, and associated works. | m3 | 7
C.2 | Selected fill and compaction: Supply and replace approved selected fill (unsieved gravel) with depth of 300mm in layers not exceeding 150 mm, water and compact each layer to the required density approved by IOM site engineer. Rate to include supply, placement, compaction, and finishing. | m3 | 4
C.3 | Reinforced concrete slab: Provide and cast 200 mm thick reinforced concrete slab (1:2:4 mix) G30 reinforced with 12 mm diameter bars at 200 mm c/c each way, top and bottom layers. Rate to include formwork, reinforcement, concrete placing, vibration, curing, and finishing; apply an approved SBR cementitious bonding agent (e.g., Sika Latex or equivalent) mixed and applied in accordance with the manufacturer's recommendations. | m3 | 2.7
C.4 | Brick stand: Construct a red brick stand measuring 3.00 m × 0.75 m × 0.80 m high, plastered on all exposed surfaces and finished with a reinforced concrete top. Rate to include all materials, labour, curing, and finishing, apply an approved SBR cementitious bonding agent (e.g., Sika Latex or equivalent) mixed and applied in accordance with the manufacturer's recommendations. | Ml | 3
C.5 | Reinforced concrete top slab on top of brick stand: Provide and cast a 100 mm thick reinforced concrete top slab measuring 3.00 m × 0.75 m, reinforced with 10 mm diameter bars at 150 mm c/c each way. Rate to include reinforcement, formwork, concrete, curing, and finishing, apply an approved SBR cementitious bonding agent (e.g., Sika Latex or equivalent) mixed and applied in accordance with the manufacturer's recommendations. | M3 | 0.34
C.6 | Gate valve chamber: Construct a one-brick thick red brick gate valve chamber with internal dimensions 1.00 m × 1.00 m × 0.60 m deep, plastered internally and externally, complete with reinforced concrete cover. Rate to include excavation, disposal of excavated material, concrete works, curing, and all associated works, apply an approved SBR cementitious bonding agent (e.g., Sika Latex or equivalent) mixed and applied in accordance with the manufacturer's recommendations. | Ls | 1
C.7 | Supply and Installation of HDPE/ G.I pipes & fittings
C.7.1 | Excavation, sand bedding with clean, coarse, well-graded sand of at least 100 mm, and backfilling of trenches for OD 63 mm PN10 HDPE pipes in any material other than rock, to a depth of 0.6 m, Includes compliance with all safety regulations regarding trench support, provision of necessary shoring, planking, and trench safety systems. | Ml | 32
C.7.2 | Supply, installation, laying, jointing, testing, and commissioning of 63 mm HDPE pipes (PE100, PN10, SDR17) per linear meter, including proper jointing by butt fusion welding . Unit rate to include all labour, materials, equipment, supervision, and incidental works required for completion. | Ml | 32
C.7.3 | Supply, installation of OD 63 stub flange complete with DN 50 backing ring, nuts and bolts & gaskets | No | 2
C.7.4 | Supply and install DN 50 flanged gate valve PN 10, suitable for OD 63 mm HDPE pipe | No | 1
C.7.5 | Supply and install DN 50 stainless steel flanged connection complete with stainless steel bolts, nuts, and washers, including full-face gasket, all necessary accessories, and fittings required for a complete, leak-proof installation. | No | 2
C.7.6 | Supply, install, test, and commission 2-inch galvanized iron (GI) pipeline, including excavation, bedding, laying, cutting, threading, welding where required, jointing, testing, backfilling, and reinstatement. The rate shall include all fittings and appurtenances such as tees, elbows, reducers, adaptors, unions, nipples, supports, and other accessories required for complete installation. All buried GI pipes and fittings shall be protected with two coats of approved anti-corrosion (anti-rust) paint before backfilling. | Ml | 9
C.7.7 | Supply and install 2-inch galvanized iron (GI) nipple, threaded at both ends, complete with sealing materials and all accessories required for a complete, leak-free installation. | No | 7
C.7.8 | Supply and install 2-inch galvanized iron (GI) 90° elbow, complete with sealing materials and all accessories required for a complete, leak-free installation. | No | 5
C.7.9 | Supply and install 2-inch galvanized iron (GI) union, complete with sealing materials and all accessories required for a complete, leak-free installation. | No | 5
C.7.10 | Supply and install 2-inch full-port galvanized iron (GI) ball valve, including cutting, threading, welding where required, connection to the pipeline, testing, and all necessary fittings and accessories to provide a complete, pressure-tight, and leak-free installation. | set | 3
C.7.11 | Supply and install 2-inch galvanized iron (GI) tee, complete with sealing materials and all accessories required for a complete, pressure-tight, and leak-free installation. | No | 2
C.7.12 | Supply and install 2-inch galvanized steel pipe support saddle/clamp, complete with galvanized anchor bolts cast into reinforced concrete, including all fixing materials required to securely support the GI pipeline in accordance with the approved drawings. | No | 6
C.7.13 | Supply and install 2-inch flexible hose, complete with two stainless steel hose clamps, connectors, and a galvanized wall-mounted hose hanger/bracket to keep the hose elevated and prevent contact with the ground when not in use. The item shall include all accessories required for complete installation and proper operation, for two points. | Ml | 20
C.7.14 | Supply, construct, and prepare a surface drainage channel from the water point to the landscaped trees, including all necessary excavation, grading, formation of the drainage path, R/C concrete with 8mm bars and masonry works where required, backfilling, compaction, and reinstatement of disturbed areas. The work shall ensure proper drainage and controlled distribution of water for irrigation of the landscaped trees without causing ponding or erosion. The rate shall include all materials, labor, equipment, fittings, and all associated civil works necessary to complete the installation in accordance with the approved drawings and the Engineer's instructions. to be assessed during the site visit. | L.s | 1
C.8 | Landscaping
C.8.1 | Supply, transport, and plant ten (10) trees at Kumur Alnayer Booster Station, including site preparation, setting out, excavation of planting pits measuring 600 mm × 600 mm × 1,000 mm deep, backfilling with approved fertile topsoil mixed with organic fertilizer, planting of healthy nursery-grown trees, initial watering, staking where required, mulching, and all necessary materials, labor, tools, and equipment. The contractor shall maintain the trees during the establishment period, including regular watering and replacement of any trees that fail to survive, to ensure healthy growth and successful establishment. to be assessed during the site visit. | No | 10
D | Clean water tank Rehabilitation
D.1 | Supply all materials, labor, equipment, and construct a 30 cm high perimeter wall around the clean water tank (dimensions: 5.8 m × 8.8 m) using first-class fired clay bricks, 200 mm (one-brick) thick, laid in 1:8 cement-sand mortar. Provide two entrance openings, each 1.0 m wide, at locations to be determined on site by the Engineer, complete with all associated civil works, and dismantle the old wall and dispose the materials. | ml | 29
D.2 | Rehabilitation of five (5) existing openings at the water tank surface by constructing 200 mm thick brickwork, 300 mm high, using first-class fired clay bricks laid in 1:8 cement-sand mortar. The work shall also include the existing manhole opening of the adjacent concrete tank. Provide and install walkable hot-dip galvanized steel grating with a serrated anti-slip surface over all openings and the manhole, including suitable frames, supports, and fixing accessories. The rate shall include all materials site prepration, fabrication, transportation, installation, and necessary civil works, complete as directed by the Engineer. Final dimensions and details shall be confirmed during the site visit. | L.S | 1
D.3 | Fabricate, supply, and install a new steel manhole cover 160 cm* 160 cm complete with a 50 × 50 × 5 mm angle frame, 3 mm mild steel cover plate, two diagonal brace from the same angle bar, heavy-duty hinges, and locking padlock 95 mm. Prepare and paint all steelwork with two coats of anti-rust paint, and one final coat of approved blue enamel. Repair defective chamber walls, including internal and external 1:6 cement-sand plaster where required, complete with all welding, fixing, and finishing works. | L.S | 1
D.4 | Thorough cleaning and removal of accumulated sludge, silt, waste, and vegetation from the clean water ground tank. The works include manual and/or mechanical desilting, collection, lifting, as well as removal of any grass or biological growth to restore full operational capacity, and safe disposal of all removed materials at an approved disposal site, in coordination with the relevant local authorities. Tank dimensions are approximately: 5.8m (outer width) × 8.8 m (length) × 3.6 m (water depth). The works shall include dewaterng, cleaning of all internal surfaces and appurtenances and reinstatement of the tank to serviceable condition, to the satisfaction of the Engineer. | L.S | 1
D.5 | Supply, install, test, and commission one Pentax CM centrifugal pump (or approved equivalent), capacity 150 L/min at 35 m head, single-phase 220 V, 50 Hz, complete with 16 A 2-pole MCB, voltage/current protector, control box, and 4 mm² copper cable installed in PVC trunking; provide fixed 2-inch PPR suction and discharge pipework, including a 3 m suction line with adequate pipe supports; install a 2-inch brass foot valve with female NPT connection and integrated mesh strainer at the suction end, a 2-inch non-return valve on the discharge line, and a 1-inch branch connection at each pump (four) complete with PPR tee, PPR ball valve union, female socket, brass valve and all required reducers, elbows, adaptors, couplings, and fittings for the priming and return line arrangement between the pump inlet and isolation valve, including all accessories necessary for a complete, tested, and fully operational installation as well as to construct a sheleter for the pump. (More details on the site visit) | LS | 1
D.6 | Supply, install, test, and commission one electromagnetic diaphragm chlorine dosing pump equivalent to Lutz-Jesco MAGDOS LB 6, with a dosing capacity of 6.3 L/h at 4 bar (6.2 L/h at 8 bar), operating on 100–240 V AC, 50/60 Hz, with a power consumption of 28 W and enclosure protection IP65. The pump shall be suitable for sodium hypochlorite dosing and supplied complete with mounting bracket, foot valve with strainer, injection valve, suction and discharge tubing, electrical cable, and all accessories required for a complete operational system. | No. | 2
D.7 | Pump House Rehabilition
D.7.1 | Supply and install a MCCB: 3-pole, 415 V, Rated current: 315 A, Breaking capacity: ≥ 36 kA , this is used as main breaker between the power supply and the pumps control unit, this should fixed in inside the control room and ensure proper fix and proper insolation and repaired the damaged cables. The scope shall include the IP65 box lockable, and all necessary accessories, including cable lugs, glands, internal wiring, and gland plate, complete work from power source for proper installation and operation. Approved Makes: ABB, Siemens, Mitsubishi Or equivalent approved. insulation using rubber-based materials (heat shrink or cold shrink type) and sealing to ensure full protection against moisture ingress. The joint should be properly aligned, mechanically secure, and fully insulated, with provision of all necessary accessories and materials | No. | 2
D.7.2 | Cleaning and rehabilitation of the booster pump house, including thorough cleaning of walls, floors, roof, and all internal surfaces, with removal of grease, dust, debris, and accumulated dirt. The works shall include repair of internal and external wall cracks and wall opening through grout and SBR, repair of floor defects, header support repair, and casting a 100 mm thick plain cement concrete floor (1:3:6 mix), finished smooth and cured in accordance with the specifications. Rehabilitate the zinc sheet roof, including holes fixing, surface preparation and application of two coats of approved anti-rust paint to the external metal surfaces and one coat to the internal surfaces. Prepare and apply textured paint to the external walls and repaint all doors, windows, and other metalwork. The scope shall also include repair or replacement of defective lighting fixtures, installation of a suitable lighting protection panel, rehabilitation of cable trunking, organization of electrical wiring and connections, and repainting of exposed metallic pipes. Remove obsolete equipment and materials in coordination with SWC and relocate them to a designated area outside the pump house. Permanently label all pumps, valves, and control panels, and arrange and rehabilitate the control panels in a neat and accessible layout. Coordinate with the electricity distribution authority where required. The rate shall include all labor, materials, equipment, and incidental works necessary to complete the rehabilitation to the satisfaction of the Engineer. | L.S | 1
D.7.3 | Dismantle the old pumps two rooms inside the booster yard; Construction of control room, including the supply of all materials, labour, equipment, and services required to complete the works in accordance with the approved technical drawings and specifications. The room shall have internal dimensions of 3×4m. • clearing the site including top soil up to 10 cm depth at whole area and removing the waste and debris away from the site as directed by the engineer. •Excavation for Foundation (Strip Foundation) for the Room boundary ( 40x 50 cm and 70 cm Depth). • Provide and construct 40 cm depth granite stone pitching, using 1:8 Cement & sand mortar. •Supply materials and build 2 bricks wall with sand cement mortar 1:6 width 40cm, and 50 cm depth under grade beamm as per drawings. •Provide & Cast Reinforced Concrete (mix 1:2:4) Grade Beam (30x30cm), reinforced with 4 Nos.12 mm bars with stirrups ø8 @20cm c/c, as per drawings. •Backfilling with selected material compacted in layers 25cm. •Supply and casting of plain concrete floor slab on ground, including base preparation, compaction, formwork if required, leveling, finishing, curing, and all related works.(ratio1:3:6). • Superstructure: • provide and Build walls by Hallow cement blocks using (1:6) cement sand mortar above the G.Beam including parapet). Rates include water and cure for 3 days minimum Door & Windows Work •Supply, fabricate and fix two panel door (120x220cm) with Sky lights made of RHS with 4 X 8cm frame, 3X6 cm for leave frame, with 1½Χ 1½ cm internal frames. security As per approved drawings • Supply, fabricate and fix one panel windows (120 X120cm) with Sky lights made of RHS square steel with3 X6 cm frame, 2X4cm for window leave, with 1½Χ 1½ cm internal frames. As per approved drawings. Supply, fabricate and fix three panel windows (120 X120cm) with Sky lights made of RHS square steel with3 X6 cm frame, 2X4cm for window leave, with 1½Χ 1½ cm internal frames. As per approved drawings. •Roof Works •Supply and installation of zinc roofing sheets with a minimum thickness of a 0.5 mm, fixed to fixed supports of 4*8 and 3*6 square pipes(2mm thickness) for the roof structure, including overlaps, fasteners and accessories, according to specifications. all steel members to be coated with antirust coating and two spray coats of oil paint to approval and all needed accessories to the satisfaction of the engineer. •Supply and apply of Plastering using cement-sand(1:6) mortar ,for walls , including surface preparation, mixing, application, leveling, finishing, curing, and all complete as per specifications. •Supply and apply internal and external painting for walls using three coats of high-quality PVA emulsion (Bomastic), including surface preparation, , sanding, and final finishing. •Supply and install Orient-brand ceiling fans, including wiring, mounting brackets, switches, and testing to ensure proper operation. •Supply and installation of 4-feet fluorescent light fittings complete with lamps, wiring, fixing accessories, testing, and commissioning. Ø500 mm industrial axial/plate fan, 400 V, 3-phase, with approximately 2,500–4,000 m³/h airflow and IP55 motor protection. industrial wall-mounted exhaust fans, each with a minimum airflow capacity of 2,500 m³/h, suitable for continuous operation in the pump room, complete with protective guards, mounting frames, electrical wiring, isolators, thermostatic control, fresh-air intake louvers, and all necessary accessories. Dismantle the two existing pumps located inside the booster yard and construct a new pump/control room of approximately 3 m × 4 m internal dimensions, including all materials, labour, equipment, transport, tools and workmanship required to complete the work. 1. Site Preparation and Foundation • Clear the site, remove vegetation, topsoil to approximately 100 mm depth, waste and debris, and dispose of the materials as directed by the Engineer. • Excavate for the strip foundation around the room perimeter, approximately 400 mm wide × 700 mm deep, or as required by the approved structural drawings. • Provide and compact approximately 400 mm thick stone/granite hardcore pitching below the floor, using suitable locally available stone. Where mortar is required, use cement-sand mortar 1:8. • Construct the foundation wall using concrete blocks/bricks with cement-sand mortar 1:6, including approximately 500 mm below finished ground level, as shown on the approved drawings. • Construct reinforced-concrete grade beam, approximately 30 × 30 cm, and lintel beam approximately 20*20cm using C25/30 concrete, reinforced with 4 No. 12 mm longitudinal bars and 8 mm stirrups at 200 mm centres. • Backfill around the foundation with selected material in layers not exceeding 250 mm and compact each layer. • Provide and cast a plain concrete floor slab, including sub-base preparation, compaction, levelling, finishing and curing. Use approximately 100 mm thick concrete, (ratio1:3:6). 2. Walls Construct the room walls using fired bricks with cement-sand mortar 1:6, including the parapet. Provide proper curing and all necessary ties, lintels and associated works. 3. Door and Windows Supply, fabricate and install one steel double-leaf door, approximately 120 × 220 cm, with RHS frame, internal framing, security locking arrangement and glazed/openable upper section as shown on the approved drawings. 4 X 8cm, 1 mm thickness frame, 3X6 cm, 1 mm thickness for leave frame, with 1½Χ 1½ cm internal frames. • • Supply, fabricate and install one steel-framed windows, approximately 100 × 120 cm each, comprising of three leaf doors, with RHS frames, internal sections, security bars/mesh where required, glazing and all fixing accessories. with3 X6 cm frame, 2X4cm for window leave, with 1½Χ 1½ cm internal frames. • Supply, fabricate and install three steel-framed windows, approximately 120 × 120 cm each, comprising of three leaf doors, with RHS frames, internal sections, security bars/mesh where required, glazing and all fixing accessories. with3 X6 cm frame, 2X4cm for window leave, with 1½Χ 1½ cm internal frames. • All steelworks shall be cleaned, primed with anti-rust primer and finished with two coats of suitable oil-based paint. 4. Roof Supply and install 0.50 mm minimum thickness galvanized/zinc roofing sheets, fixed to a steel roof frame using approximately 8 × 4 cm and 6 × 3 cm RHS sections, minimum 2 mm thickness, including purlins, overlaps, self-drilling screws, washers, flashing and all accessories, including foam thermal insulation. All exposed steel members shall receive one suitable anti-corrosion primer coat and two finishing coats of oil-based paint. 5. Plastering and Painting Apply cement-sand plaster, 1:6, to internal and external wall surfaces, including preparation, levelling, finishing and curing. Apply three coats of good-quality exterior/interior emulsion paint and weather texture paint, including surface preparation, sanding, primer where required and final finishing. 6. Electrical and Lighting Supply and connect power to the room from the nearest suitable power source, including all necessary electrical installation works in accordance with good electrical practice. Provide 4 mm² cable from the source and a 2-pole, 25 A MCB complete with enclosure. Install three (3) 17 A switches, including 2.5 mm² wiring, conduits/supports, accessories, testing and commissioning. Supply and install 4-ft LED industrial light fittings, complete with lamps, 1.5 mm² wiring, conduits/supports, switches, accessories, testing and commissioning. Supply and install one (1) 80 W ceiling fan, complete with 1.5 mm² wiring, supports, switch, accessories, testing and commissioning. 7. Pump Room Ventilation Supply and install two industrial wall-mounted axial exhaust fans, approximately 500 mm diameter, 400 V, 3-phase, 50 Hz, with a minimum airflow of approximately 2,500 m³/h per fan, suitable for continuous operation and with suitable motor protection. Each fan shall include protective guard, mounting frame, local isolator, wiring, thermostat/temperature control and all accessories. 8. Pump Maintenance Provisions Provide a floor slope and drain/sump arrangement to allow removal of water from leakage, washing and maintenance activities. Provide and prepare wall penetrations for the two pump connections, including openings through the concrete tank slab where required. Carry out all necessary cutting, making good, fixing, protection, and sealing around the penetrations using suitable waterproof sealant, complete with all associated work | L.S | 1
D.8 | Albilihab
D.8.1 | Dismantle the existing pump and hand it over to SWC outside the pump house. Supply, installation, testing, and commissioning of a heavy-duty horizontal split-case double suction centrifugal pump for raw water application, complete with electric motor, base frame/ chases, coupling- wool coupling with a band width of less than 10 cm, coupling guard, and accessories, no new pipe supply is included, fusion welding for the piping system. Detailed Specifications: Duty Point: Q = 180 m³/h, H = 70 m. Mounting: Supply, cast, and cure a reinforced concrete foundation of minimum C25/30 concrete. Foundation dimensions shall be based on the pump manufacturer's certified foundation drawing, with sufficient projection beyond the base frame on all sides. Foundation thickness shall be approximately 300 mm, or as required to align the pump suction centerline with the existing suction pipeline. Anchor bolts, sleeves, non-shrink grout, leveling, and alignment shall be included. Type: Horizontal Split Case, Double Suction Centrifugal Pump Impeller: Closed, dynamically balanced; Speed: Approximately 1450 RPM at 50 Hz. Minimum Pump Efficiency: Not less than 80% at the specified duty point. Materials of Construction: Casing: Cast Iron EN, internally coated with epoxy coating, minimum 200 microns DFT; Impeller: Stainless Steel ASTM (AISI 316 equivalent); Shaft: Stainless Steel AISI or equivalent conforming to ASTM A276; Shaft Seal: Gland Packing (soft packing suitable for raw/silt-laden water). Pipe at the Suction Line: Existing HDPE PE100 SDR17 PN10 pipeline, DN200, the pipe already exists; pricing shall cover only the hookup pipe supports, flanges, backing rings/adaptors, gaskets, fasteners, and all fittings required for pump. Fittings at Suction Line: Flanged full-bore Foot Valve, Ductile Iron body with integral Stainless-Steel strainer, DN200 PN10; flanged eccentric reducer (flat side up) from DN200 to the pump suction flange; 90-degree long-radius elbows, pressure-rated fittings compatible with the piping system. Pipe at the Discharge Line: Existing HDPE PE100 SDR17 PN10 pipeline, 160 mm, connection of the pump discharge to the existing 160 mm HDPE pipeline using all necessary fittings and accessories, including civil work, HDPE stub flange, backing ring, gaskets, stainless steel bolts, nuts, washers, adaptors, and any additional materials required for a complete installation testing the line for leak. Fittings at Discharge Line: 90-degree long-radius elbows Adapters, Flanged concentric reducer pn 16, pressure-rated fittings compatible with the piping system, DN150 Gate valve PN 16 and NRV DN 150 PN 16 with all accessories. Motor Power: 55 kW; Motor Speed: Approximately 1450 RPM at 50 Hz. Motor Specifications: Type: Three-phase Squirrel Cage Induction Motor; Cooling: TEFC (Totally Enclosed Fan Cooled); Protection Class: IP55. Scope of Supply: Supply, install, align, test, and commission a complete pump unit on base frame for, including TEFC motor, flexible coupling with coupling guard, suction and discharge hookup piping with fittings, pipe supports (as determined on site), flanges, backing rings/adaptors, gaskets, fasteners, and all accessories necessary for a complete installation. Suction and discharge pipework shall be independently supported so that no external loads are transmitted to the pump flanges. Pumps and control boxes shall be clearly labeled. The tenderer shall submit certified pump performance curves, including Head vs. Flow, Efficiency, Brake Power, and NPSH Required at 180 m³/h, and shall verify that the selected pump satisfies the specified duty point considering all pipeline and fitting losses. (More details on the pump hookup will be provided after the site visit.) | No. | 1
D.8.2 | Supply, installation, testing, and commissioning of an IP54 wall-mounted star–delta starter control panel with mechanical and electrical interlocks between the star and delta contactors, suitable for a 55 kW, 415 V, 3-phase pump motor, complete with a 160 A, 3P MCCB main isolator; AC-3 rated contactors comprising one (1) 115 A main contactor, one (1) 65 A delta contactor, and one (1) 50 A star contactor; adjustable electronic star–delta timer; thermal overload relay (90–110 A adjustable range), installed in the main line and set in accordance with the motor manufacturer's nameplate full-load current. The control circuit shall include a 6–10 A, 1P MCB, 220–240 V AC control voltage, phase failure and phase sequence relay, auxiliary relays, Start and Stop push buttons, emergency stop push button, Auto/Manual selector switch (where required), Power ON, Star, Delta, and Trip indication lamps, one analog ammeter complete with current transformer, one analog voltmeter with selector switch, and all necessary control devices. The panel enclosure shall be fabricated from powder-coated sheet steel with a minimum protection rating of IP54 and shall be wall-mounted using M14 expansion anchors (Fischer or approved equivalent). The scope shall include complete factory wiring, ferruling, labeling, terminal blocks, cable glands, cable lugs, termination to the motor and incoming power supply, testing, commissioning, functional verification of the star–delta sequence, insulation resistance testing, and provision of all accessories and minor materials required to deliver a complete and fully operational system. The star–delta control panel shall be connected to the power supply and connected to the motor using the existing and new cables and to be connected using an approved straight-through joint kit, complete with proper mechanical and electrical connectors, followed by insulation using rubber-based materials (heat shrink or cold shrink type) and sealing to ensure full protection against moisture ingress. The joint should be properly aligned, mechanically secure, and fully insulated, with provision of all necessary accessories and materials. | No. | 1
D.8.3 | Supply and install of reinforced copper cable, 3.5C × 25 mm² XLPE/SWA/PVC power cable, 0.6/1 kV, including cable laying on tray and routing to ground level, proper termination with lugs, dressing and connection to the motor, gland installation at the control panel and hings, and complete connection to the control panel, all in accordance with project specifications, this is for the new pumps inside the Booster. | ML | 25
D.9 | Jabal Moya
D.9.1 | Dismantle the existing pump and hand it over to SWC outside the pump house. Supply, installation, testing, and commissioning of a heavy-duty horizontal split-case double suction centrifugal pump for raw water application, complete with electric motor, base frame/ chases, coupling- wool coupling with a band width of less than 10 cm, coupling guard, and accessories, no new pipe supply is included, fusion welding for the piping system. Detailed Specifications: Duty Point: Q = 180 m³/h, H = 70 m. Mounting: Supply, cast, and cure a reinforced concrete foundation of minimum C25/30 concrete. Foundation dimensions shall be based on the pump manufacturer's certified foundation drawing, with sufficient projection beyond the base frame on all sides. Foundation thickness shall be approximately 300 mm, or as required to align the pump suction centerline with the existing suction pipeline. Anchor bolts, sleeves, non-shrink grout, leveling, and alignment shall be included. Type: Horizontal Split Case, Double Suction Centrifugal Pump Impeller: Closed, dynamically balanced; Speed: Approximately 1450 RPM at 50 Hz. Minimum Pump Efficiency: Not less than 80% at the specified duty point. Materials of Construction: Casing: Cast Iron EN, internally coated with epoxy coating, minimum 200 microns DFT; Impeller: Stainless Steel ASTM (AISI 316 equivalent); Shaft: Stainless Steel AISI or equivalent conforming to ASTM A276; Shaft Seal: Gland Packing (soft packing suitable for raw/silt-laden water). Pipe at the Suction Line: Existing HDPE PE100 SDR17 PN10 pipeline, DN200, the pipe already exists; pricing shall cover only the hookup pipe supports, flanges, backing rings/adaptors, gaskets, fasteners, and all fittings required for pump. Fittings at Suction Line: Flanged full-bore Foot Valve, Ductile Iron body with integral Stainless-Steel strainer, DN200 PN10; flanged eccentric reducer (flat side up) from DN200 to the pump suction flange; 90-degree long-radius elbows, pressure-rated fittings compatible with the piping system. Pipe at the Discharge Line: Existing HDPE PE100 SDR17 PN10 pipeline, 160 mm, connection of the pump discharge to the existing 160 mm HDPE pipeline using all necessary fittings and accessories, including civil work, HDPE stub flange, backing ring, gaskets, stainless steel bolts, nuts, washers, adaptors, and any additional materials required for a complete installation testing the line for leak. Connect the existing DN160 HDPE PE100 SDR17 PN10 discharge line to the existing DN250 main line by removing the old metallic saddle and installing a new DN250 × DN160 HDPE reducing tee. The price shall include pipe cutting and preparation, HDPE fusion welding, flanges/stub ends, backing rings, gaskets, bolts, supports, minor civil works, testing, and all necessary fittings and accessories for a complete leak-free connection. No new straight pipe supply is included. Fittings at Discharge Line: 90-degree long-radius elbows Adapters, Flanged concentric reducer pn 16, pressure-rated fittings compatible with the piping system, DN150 Gate valve PN 16 and NRV DN 150 PN 16 with all accessories. Motor Power: 55 kW; Motor Speed: Approximately 1450 RPM at 50 Hz. Motor Specifications: Type: Three-phase Squirrel Cage Induction Motor; Cooling: TEFC (Totally Enclosed Fan Cooled); Protection Class: IP55. Scope of Supply: Supply, install, align, test, and commission a complete pump unit on base frame for, including TEFC motor, flexible coupling with coupling guard, suction and discharge hookup piping with fittings, pipe supports (as determined on site), flanges, backing rings/adaptors, gaskets, fasteners, and all accessories necessary for a complete installation. Suction and discharge pipework shall be independently supported so that no external loads are transmitted to the pump flanges. Pumps and control boxes shall be clearly labeled. The tenderer shall submit certified pump performance curves, including Head vs. Flow, Efficiency, Brake Power, and NPSH Required at 180 m³/h, and shall verify that the selected pump satisfies the specified duty point considering all pipeline and fitting losses. (More details on the pump hookup will be provided after the site visit.) | No. | 1
D.9.2 | Rehabilitation of the existing star–delta starter control panel by inspecting, cleaning, repairing, and restoring it to full operating condition. Replace all defective or damaged components, including contactors, MCCB, overload relay, timer, relays, push buttons, selector switches, indicating lamps, meters, terminal blocks, internal wiring, cable glands, and other items as required. Securely mount the panel using M14 expansion anchors (Fischer or approved equivalent). The work shall include rewiring where necessary, ferruling, labeling, cable termination with compression lugs, and replacement of damaged terminal blocks and accessories cable connection. Complete insulation resistance, continuity, protection, and functional tests, followed by commissioning to verify correct star–delta operation. The rate shall include all labor, materials, consumables, tools, and incidental works required to deliver a safe, reliable, and fully operational control panel. | No. | 1
D.10 | 4 villages/Algarbi
D.10.1 | Dismantle the existing pump and hand it over to SWC outside the pump house. Supply, installation, testing, and commissioning of a heavy-duty horizontal split-case centrifugal pump for raw water application, complete with electric motor, base frame/ chases, coupling- wool coupling with a band width of less than 10 cm, coupling guard, and accessories, no new pipe supply is included, fusion welding for the piping system. Detailed Specifications: Duty Point: Q = 200 m³/h, H = 75 m. Mounting: Supply, cast, and cure a reinforced concrete foundation of minimum C25/30 concrete. Foundation dimensions shall be based on the pump manufacturer's certified foundation drawing, with sufficient projection beyond the base frame on all sides. Foundation thickness shall be approximately 300 mm, or as required to align the pump suction centerline with the existing suction pipeline. Anchor bolts, sleeves, non-shrink grout, leveling, and alignment shall be included. Type: Horizontal Split Case, Double Suction Centrifugal Pump Impeller: Closed, dynamically balanced; Speed: Approximately 1450 RPM at 50 Hz. Minimum Pump Efficiency: Not less than 80% at the specified duty point. Materials of Construction: Casing: Cast Iron EN, internally coated with epoxy coating, minimum 200 microns DFT; Impeller: Stainless Steel ASTM (AISI 316 equivalent); Shaft: Stainless Steel AISI or equivalent conforming to ASTM A276; Shaft Seal: Gland Packing (soft packing suitable for raw/silt-laden water). Pipe at the Suction Line: Existing HDPE PE100 SDR17 PN10 pipeline, DN250, The pipe already exists; pricing shall cover only the hookup pipe supports, flanges, backing rings/adaptors, gaskets, fasteners, and fittings required for pump installation and future removal. Fittings at Suction Line: Flanged full-bore Foot Valve, Ductile Iron body with integral Stainless-Steel strainer, DN250 PN10; flanged eccentric reducer (flat side up) from DN250 to the pump suction flange; 90-degree long-radius elbows, pressure-rated fittings compatible with the piping system. Pipe at the Discharge Line: Existing HDPE PE100 SDR17 PN10 pipeline, DN200. The pipe already exists; pricing shall cover only the hookup pipe supports, removable flanged spool pieces, flanges, backing rings/adaptors, gaskets, fasteners, and fittings. Fittings at Discharge Line: 90-degree long-radius elbows Adapters, pressure-rated fittings compatible with the piping system, Gate valve 200 DN PN 16 NRV DN 200 PN 16 with all accessories , Flanged concentric reducer pn 16 where required. Motor Power: 75 kW; Motor Speed: Approximately 1450 RPM at 50 Hz. Motor Specifications: Type: Three-phase Squirrel Cage Induction Motor; Cooling: TEFC (Totally Enclosed Fan Cooled); Protection Class: IP55. Scope of Supply: Supply, install, align, test, and commission a complete pump unit on base frame for, including TEFC motor, flexible coupling with coupling guard, suction and discharge hookup piping with fittings, pipe supports (as determined on site), flanges, backing rings/adaptors, gaskets, fasteners, and all accessories necessary for a complete installation. Suction and discharge pipework shall be independently supported so that no external loads are transmitted to the pump flanges. Pumps and control boxes shall be clearly labeled. The tenderer shall submit certified pump performance curves, including Head vs. Flow, Efficiency, Brake Power, and NPSH Required at 200 m³/h, and shall verify that the selected pump satisfies the specified duty point considering all pipeline and fitting losses. (More details on the pump hookup will be provided after the site visit.) | No. | 2
D.10.2 | Supply, installation, testing, and commissioning of an IP54 wall-mounted star–delta starter control panel with mechanical and electrical interlocks between the star and delta contactors, suitable for a 75 kW, 415 V, 3-phase pump motor, complete with a 200 A, 3P MCCB main isolator; AC-3 rated contactors comprising one (1) 185 A main contactor, one (1) 95 A delta contactor, and one (1) 80 A star contactor; adjustable electronic star–delta timer; thermal overload relay (125–160 A adjustable range), installed in the main line and set in accordance with the motor manufacturer's nameplate full-load current. The control circuit shall include a 6–10 A, 1P MCB, 220–240 V AC control voltage, phase failure and phase sequence relay, auxiliary relays, Start and Stop push buttons, emergency stop push button, Auto/Manual selector switch (where required), Power ON, Star, Delta, and Trip indication lamps, one analog ammeter complete with current transformer, one analog voltmeter with selector switch, and all necessary control devices. The panel enclosure shall be fabricated from powder-coated sheet steel with a minimum protection rating of IP54 and shall be wall-mounted using M14 expansion anchors (Fischer or approved equivalent). The scope shall include complete factory wiring, ferruling, labeling, terminal blocks, cable glands, cable lugs, termination to the motor and incoming power supply, testing, commissioning, functional verification of the star–delta sequence, insulation resistance testing, and provision of all accessories and minor materials required to deliver a complete and fully operational system. The star–delta control panel shall be connected to the power supply and connected to the motor using the new cables. | No. | 2
D.10.3 | Supply and install of reinforced copper cable, 3.5C × 25 mm² XLPE/SWA/PVC power cable, 0.6/1 kV, including cable laying on tray and routing to ground level, proper termination with lugs, dressing and connection to the motor, gland installation at the control panel and hings, and complete connection to the control panel, all in accordance with project specifications, this is for the new pumps inside the WTP. | ML | 76
E | DN300 carbon steel discharge header complete with welding, flanged connections, alignment, and supports
E.1 | Dismantling, removal, and safe disposal off-site of the existing discharge header system from pumps to the valve end, including all pipes (steel/RC embedded sections), buried and wall-embedded parts (sleeves, anchors, and cast-in components), fittings, supports, valves, bolts, and associated accessories. Works shall include cutting, lifting, handling, and removal without damaging adjacent structures and close the branches that are not needed, and reinstatement of affected areas where required, and change the location of one the old pumps. | LS | 1
E.2 | Supply, fabricate, and install DN200 (8") welded stub-in branch connections on the DN300 carbon steel header using ASTM A53 Grade B Schedule 40 pipe. The work shall include cutting and preparing the existing DN300 pipe, fabrication of branch openings, welding of the branch connections, installation of reinforcement supports , grinding, cleaning, inspection, and all necessary fittings, consumables, labor, tools, and equipment to complete the work. For the two pump branches at the existing locations of old pumps , each branch shall have an external length of 1.5 m, measured from the rear face of the DN300 pipe to the flange face. | m | 3
E.3 | Supply and install PN16 12 holes weld neck flanges Stainless Steel (304 / 316) DN200 Including rubeer gaskets and stainless steel bolts size M24, nuts, washers, and alignment; complete with welding and fittings. | No. | 2
E.4 | Dismantle the old one, Supply and install Stainless blind flangesDN 300 EN1092-1, PN16, end caps ncluding rubeer gaskets and stainless steel bolts size M24, nuts, washers, and alignment. and all fittings required to complete the header. | No. | 1
E.5 | Supply and construct C30/37 reinforced-concrete pipe supports complete with fabricated carbon-steel saddles for the DN300 main header and DN200 pump branches. The supports shall be provided at four (4) locations: S-1: replace the old support approximately 300 mm from the left DN300 blind flange. S-2: replace the old support S-3: at the 200 mm branches. S-4: at the 200 mm branches. RC supports: S-1 to S-5: min of 600 × 600 × 500 mm for DN300 pipe. S-6 to S-8: min of 500 × 500 × 450 mm for DN200 pipe. Concrete: C30/37 minimum. Reinforcement: high-yield steel, with spacing and arrangement as per drawing and approved by the Engineer. Minimum concrete cover: 50 mm. Supports shall be properly founded or securely anchored adhsive to the existing concrete slab where the existing structure is confirmed adequate. Metallic saddles: For DN300 pipe: Pipe outside diameter: 323.9 mm. Saddle material: ASTM A36 or S275 carbon steel. Saddle plate thickness: 10 mm minimum. Saddle width: 200 mm minimum. Bearing angle: approximately 120° (60° each side). Provide 10 mm neoprene/rubber liner between the saddle and pipe. Provide stiffeners and suitable anchor bolts as required. For DN200 pipe: Pipe outside diameter: 219.1 mm. Saddle material: ASTM A36 or S275 carbon steel. Saddle plate thickness: 10 mm minimum. Saddle width: 150 mm minimum. Bearing angle: approximately 120° (60° each side). Provide 10 mm neoprene/rubber liner between the saddle and pipe. Provide stiffeners and suitable anchor bolts as required. Steel saddles shall be protected with zinc-rich primer and epoxy/polyurethane coating. Saddles shall be accurately positioned, leveled, and aligned and shall not restrict required pipe movement. Where supports are fixed to an existing concrete slab, drilling and chemical/mechanical anchoring shall only be carried out after confirming the condition and thickness of the existing concrete. The price shall include C30/37 concrete, reinforcement, formwork, foundations/anchoring, steel saddles, stiffeners, anchor bolts, rubber/neoprene liners, protective coating, installation, alignment, curing, and all necessary materials and labor. | LS | 1
E.6 | Internal lining of all carbon steel header pipes shall be provided with a potable water approved epoxy coating in accordance with AWWA C210 or equivalent EN/ISO standard suitable for drinking water applications. Surface preparation to a minimum standard with ISO 8501-1. External protection for all buried or underground steel pipe sections shall be provided using an approved anti-corrosion coating system suitable for soil burial conditions, complying with ISO 12944 and/or equivalent EN standards, consisting of primer, intermediate, and finish protective layers. All coating works shall include inspection | LS | 1
E.7 | Hydrostatic testing of complete system at 1.5 × working pressure including flushing and cleaning, Commissioning and handover of complete pumping header system. | LS | 1
F | Chamber construction/ Rehabilitation and concrete works
F.1 | Rehabilitation of the 12-inch valve of the valve chamber, comprising repair of damaged surfaces and all related civil works and prepration and Cast plain cement concrete using mix ratio of 1:3:6 for the floor thick nes of 15 cm , re-plastering interna and external walls with cement-sand mortar using a mix ratio of 1:8, and repair and repainting of the chamber cover with approved protective paint. | LS | 1
F.2 | Chamber Construction and Rehabilitation: Construct a valve chamber using first-class fired red brick masonry for a DN300 control valve, with minimum internal dimensions of 1.50 m × 1.50 m × 1.50 m, in accordance with the approved drawings and specifications. The work shall include complete demolition and removal of the existing chamber, disposal of debris, excavation, dewatering, disposal of unsuitable materials, backfilling and compaction, reinforced concrete works, brick masonry, internal and external plastering, drainage provisions, access steps, pipe penetration sealing using approved waterstops or flexible sealant boots/Styrofoam, and all finishing works. Provide a 100 mm thick reinforced concrete cover slab reinforced with 10 mm bars at 200 mm c/c each way and two side lifting hooks shall be provided for safe lifting and handling of the cover, with a 650 × 650 mm manhole opening fitted with a 5 mm thick hot-dip galvanized steel lockable cover. Rate shall include all labour, materials, equipment, testing, site reinstatement, and incidentals required for a complete and operational chamber in accordance with international standards and UN technical requirements. | No | 1
G | Safety and Fire Resistance Equipment
G.1 | Supply and installation of trolley-mounted CO₂ (Carbon Dioxide) fire extinguishers, each with a 30 kg capacity, suitable for extinguishing Class B fires and fires involving energized electrical equipment, including all necessary accessories and a robust wheeled trolley. The extinguishers shall be brand new, fully charged, certified, and suitable for energized electrical equipment, with the applicable fire classification and certification clearly marked on each unit. Each unit shall include a suitable discharge hose/horn, safety pin, tamper seal, operating valve and trolley, and shall comply with applicable BS EN 1866-1 or equivalent requirements. The Contractor shall provide basic operational training to the pump operator on the safe and correct use of CO₂ fire extinguishers. Training shall be conducted using a separate extinguisher designated for training purposes and shall not involve discharging the installed units. | No | 2
H | Signboard
H.1 | Supply, fabrication, transportation, and installation of a project signboard comprising four (4) steel panels, each measuring 150 × 30 cm, mounted on a steel frame fabricated from 60 × 30 mm box section steel, 3 mm thick. The signboard panels shall be manufactured from 1.2 mm thick steel sheets, with a clear 80 mm gap between adjacent panels. The panels shall be fixed to steel support legs fabricated from 3-inch (75 MM) DIAMETER Circular steel pipe, 3 mm thick wall thickness, securely anchored into two (2) pits, each measuring 50 × 50 × 50 cm, using plain concrete (1:3:6 mix). The item shall include surface preparation, application of an anti-rust primer, and three coats of oil-based paint, finished with a white background and blue lettering, in accordance with the approved mock-up drawings and the directions of the IOM Engineer. The rate shall include all materials, accessories, labor, tools, equipment, transportation, and complete installation, fully finished and ready for use. | No | 1
TOTAL COST

## Two(2) stances toilet block
Bill of Quantities ( BOQ)
Project Name : Sudan Integrated Social Sector Infrastructure Rehabilitation Project (SISSIRP) Project Type : WASH Project Locations: Sennar , Jebal Moya Staff's(2) stances toilet blocK- at Kamar Al-Nayer booster. Project Duration: days
General Guidelines
1 | Design plans and BoQ are complementary to each other, hence the contractor has the obligation to execute the tasks mentioned in either one of them. Accordingly The contractor's shall include all what is mentioned in the drawings & all what is mentioned in the BOQs. Incase BOQ and technical drawings have discrepancies. BOQ supersedes technical drawings. Follow IOM site engineers site instruction at all times.
2 | All the BoQ articles comprise supplying manpower, machinery, equipment, transportation all necessary requirements to get the work done properly regardless of it's mentioned in the BoQ articles or not.
3 | In case that there is any item or detail in the drawings not mentioned in the BOQ (or vise versa) then this item or detail is considered included in the contractor's price for this project & he should execute it within his contract price without claiming any increase to the contract price, as it is considered part of the contract.
4 | All the BoQ articles must be carried out according to the guidelines of Sudanese Technical Specifications, with updates and instructions of IOM Engineer.
5 | All the BoQ articles comprise removing and transporting any debris or rubble to allocated disposal areas by municipality or local authority.
6 | The Contractor must obtain prior written approval from the IOM Programme Manager and the Procurement Unit for any cost-related Variation Orders. IOM Engineer will record and justify any variations to both parties. No VO shall be implemented without the Programme Manager's written approval.
7 | Site visit is required for vendor to see / inspect project, and to submit a letter mentioning site been visited with tendering documents.
8 | Follow IOM Engineer's instruction at all times.
9 | Submit work plan schedule for project activities.
Technical Specifications:
1 | The price includes all required materials, fittings , accessories , tools , machines , instruments, labor works with all the requirements, installing , testing and commissioning and put in operation to get the system work properly as per international specifications , beneficiary and IOM engineer instructions and to complete the works as stated in the contract items , shop drawings , details and complete the work in all aspects.
2 | Supplying of materials shall not be done before getting IOM Engineer's approval on the materials type, also the contractor should provide certificate of origin and tests result certificate for the supplied materials
3 | All materials should be a good quality and the brand and origin should be subject to the approval of IOM Engineer . Show sample for IOM Engineer's approval before installing. Cost include transportation and installation. Follow IOM Engineer's instruction during installation.
4 | Any damaged parts in any system or structure due to the work in the site , will be responsibility of contractor to redo poor workmanship without cost to IOM .
5 | Contractor / vendor is responsible to delivered all the works to local authority,beneficiary as well as IOM Engineer.
6 | Curing for all concrete works should be maintaied 24 hours, the curing should be not less than 7 days before construction start above any concrete structure
7 | Cleaning the site from any debris during and after complete all the work.
8 | The Contractor shall equip all materials, workers and equipment necessary for the performance of the work specified in the Bill of Quantities and Drowings in all its aspects.
9 | All Electrical connection shall be tested and commissioned before handover to IOM Engineer
10 | The company will be responsible for getting all approval documents from the government authorities in the State
11 | All the fees for materials transport handling and testing of samples should be paid by the Contractor if it mentioned in the BoQ or not.
12 | The Contractor implementing this project should hire laborers and workers from the Locality as much as possible.
# | Description of Work | Unit | Quantity | Unit Rate USD | Amount USD | Remarks
1 | General
A | Mobilization and Demobilization
A.1 | Mobilization and demobilization of vehicles, tools, materials and personnel required for the works, including transport of technical and administrative teams to site. Works include site preparation—leveling, backfilling, and grading—and provision of temporary facilities such as shelters, water supply, and HSE amenities. All activities shall be carried out under qualified engineering supervision using approved materials in accordance with standard specifications. | L.S | 1
2 | Two(2) stances toilet block
B | Substructure
B.1 | Excavation of a pit with internal dimensions of 4.7m*2.7m*2.5m depth (Septick tank). The bottom of the excavation must be trimmed, leveled and compacted to receive the base layer, and the Contractor must adhere to all safety regulations and local standards throughout the work. all suitable excavated materials shall be used to form backfilling with proper compaction. | m3 | 32
B.2 | Supply materials and cast a plain concrete with a thickness of 10 cm(1:3:6) on the prepared and approved subgrade. | m2 | 12.7
B.3 | Provide & Cast Reinforced Concrete 1:2:4 floor slab for septic with 20 cm thickness reinforced with 12mm bars 15cm c/cin both directions (top and bottom layer). Rates to include for form work, workmanship and curing as directed by the engineer . Concrete shall be mechanically mixed, placed and vibrated. | m3 | 2.54
B.4 | Supply and Construction of 1/2 brick shuttering Wall (two sides of RC wall) with cement sand mortar1:6 : includes, using approved bricks and cement sand mortar, complete with alignment, bonding, curing, and all necessary workmanship as per drawings. rate Inclusive divided walls | m2 | 30
B.5 | supply materials and cast R.C(mix1:2:4) side walls with T12 @15cm c/c (Horizontal & vertical)thickness15cm. Rates include form work, workmanship and curing for7 days min. as directed by theengineer. | m3 | 6
B.6 | Supply and apply Plastering of cement-sand(1:6) mortar ,for walls , including surface preparation, mixing, application, leveling, finishing, curing, and all complete as per specifications.The pit lining should extend 50 CM above the ground level. | m2 | 35
B.7 | Supply and implement waterproofing for the pit walls using an approved bituminous flancoat material, provided that the surface is cleaned well from dust and mortar residues, then at least three layers of flancoat are painted, taking into account the overlapping of the layers and the perpendicularity of the direction of the paint, in accordance with the engineer’s instructtions and approved technical specifications. | m2 | 35
B.8 | Supply materials and cast reinforced concrete for cover slab with thickness of 15cm(1:2:4).Reinforcement shall consist of 12 mm diameter steel bars spaced (15cm c/c)apart in both directions (top or bottom layer). Concrete shall be mechanically mixed, placed and vibrated. the rate include (3)inspection opening as per drawings. | m3 | 2
C | Toilet Foundation
C.1 | Strip foundation for the toilet Walls:Excavate Strip Foundation with dimension 50cmx40x70cm depth. | ML | 11
C.2 | Supply materials and Lay stone for strip foundation with granite stone masonry stone using cement sand mortar 1:6 width 40cm, and 50 cm depth as per drawings with best workmanship. | m3 | 3
C.3 | Supply materials and build 2 bricks wall with sand cement mortar 1:6 width 40cm, and 50 cm depth under gradebeam. | ML | 10
C.4 | Backfilling: spupply selected materials and backfill in layers 25cm, watered and compacted to achieve relative density 95%, according to the engineer instructions. | m3 | 7
C.5 | Soak Away Pit: excavate effluent soak- away well with diameter of 2m x 2.5m depth (depends on lowes summer water table), rimmed with burnt clay bricks, header bond(cement: sand) mortar, filled with graded hardcore , covered by a sheet of polyethylene or iron sheet and buried. | LS | 1
D | Sanitary Plubming system
D.1 | Supply , lay and connect PVC waste drainage pipes (PVC 8-inch,6inh, 4inch). The rate inclusive digging trenches, cuttings , threading, joining with all necessary fittings branches , elbows, bends ,tees plugs unions and clips. | LS | 1
D.2 | Provide materials and build one brick wall manholes of sizes (60x60cm and 45x45cm)with invert levels,rate shall include gully trap (30x30) cm. . The rate shall include excavation, backfilling, plastering and provide heavy duty covere for manholes. | LS | 1
E | Superstructure (toilet dimensions 1.7x2.C/C for each)
E.1 | Supply materials and Construction Masonry Walls (one Brick Thick) with Cement Mortar1:6 the rate includes parapet. | m2 | 40
E.2 | Supply and apply an SBR-modified cement mortar screed (1:6 cement:sand mix) to provide the required slope for effective rainwater drainage. SBR bonding agent shall be added at a rate of 2 litres per 50 kg bag of cement, or as recommended by the manufacturer | m3 | 0.5
E.3 | Supply material and cast in situ reinforced concrete tie beam(slab beam) of size 20cm x20cm with 4 Nos. 12 mm bars and stirrups of ø8 mm@ 20cm c/c. Concrete shall be mechanically mixed, placed and vibrated. | ml | 14
E.4 | Provide & Cast Reinforced Concrete 1:2:4 slab for toilet roof with 15 cm thickness reinforced with 12mm bars 15cm c/cin both directions (top and bottom layer). Rates to include for form work, workmanship and curing as directed by the engineer . Concrete shall be mechanically mixed, placed and vibrated. | m3 | 1.2
E.5 | Supply and apply of Cement Plastering includes cement-sand(1:6) mortar ,for walls , including surface preparation, mixing, application, leveling, finishing, curing, and all complete as per specifications. | m2 | 90
E.6 | Supply and apply internal and external painting for walls using three coats of high-quality PVA emulsion (Bomastic), including surface preparation, , sanding, and final finishing. | m2 | 45
E.7 | Supply and apply three coats of high-quality exterior acrylic weather-resistant paint to external textured walls, including surface preparation, cleaning, crack filling where required, priming, and final finishing, complete. | m2 | 45
E.8 | Supply and install walls ceramic tiles size 40 × 40 cm Tile type and quality shall be approved by the engineer based on a submitted sample. Work includes mortar bedding, grouting, leveling, and finishing | m2 | 6
E.9 | Supply materials and install water flush toilet seat(eastern type) complete with cistern and all accessories(Angle valve, shaft, …etc) and necessary fittings, pipe connections. | no. | 2
E.10 | Supply and installation of LED Light at least 56 W complete with lamps, wiring, fixing accessories, testing, and commissioning. | no. | 4
E.11 | Supply and install exhaust fan for bathrooms , each with dimensions 40 cm × 40 cm. The item includes wall opening preparation, mounting, electrical connections, sealing, and testing to ensure proper operation as approved by the engineer. | no. | 2
E.12 | Supply and installation of steel doors fabricated from square steel pipes (8x4 and 6x3), covered with heavy gauge steel sheets, including frames, hinges, locks, painting, and installation of fiberglass skylights (door size 0.8m*2.1m). | no. | 2
E.13 | Supply and install PPR (Hot-Welded) fresh water pipes, 1-inch diameter, extending from the water tank to toilte , The work includes hot welding, installation of fittings such as elbows, tees, unions, couplings, and all necessary accessories. | ml | 20
E.14 | Supply and install fiber glass water tank(vertical) of capacity 500-liter (Tiga brand or equivelant), three-layer, with 1 inch PPR inlet and outlet connections and valves, cover, and accessories as well as all necessary plumbing connections from main WTP line and down to toilets. | no. | 2
E.15 | Construct and install new concrete entrance steps, including excavation, formwork, concrete, finishing, and all associated works, complete. | LS | 1
E.16 | Supply and install a complete shower unit, including shower head, pipework, valves, drainage connection, and all necessary fittings and accessories, complete in all respects. | LS | 1
F | Signboard
F.1 | Project signboard: Supply, fabrication, transportation, and installation of a project signboard measuring 80 × 60 cm, mounted on a steel frame fabricated from 60 × 30 mm box section steel, 3 mm thick. The signboard panels shall be manufactured from 1.2 mm thick steel sheets with a diagonal brace from the same frame box section The panels shall be fixed to Toilet exterior wall, and securely anchored using four Fischer bolts m12 using Cleat angle welded to the frame (1.25 inch) The item shall include surface preparation, application of an anti-rust primer, and three coats of oil-based paint, finished with a white background and blue lettering, in accordance with the approved mock-up drawings and the directions of the IOM Engineer. The rate shall include all materials, accessories, labor, tools, equipment, transportation, and complete installation, fully finished and ready for use. | No | 1
TOTAL COST

## Rehab of main transmission line
Bill of Quantities ( BOQ)
Project Name : Sudan Integrated Social Sector Infrastructure Rehabilitation Project (SISSIRP) Project Type : WASH Project Locations: Sennar , Sennar, Rehabilitation of main transmisssion line, 22 Km Project Duration: days
General Guidelines
1 | Drawings and BoQ are complementary to each other, hence the contractor has the obligation to execute the tasks mentioned in either one of them. Accordingly The contractor's shall include all what is mentioned in the drawings & all what is mentioned in the BOQs. Incase BOQ and technical drawings have discrepancies. BOQ supersedes technical drawings. Follow IOM site engineers site instruction at all times.
2 | All the BoQ articles comprise supplying manpower, machinery, equipment, transportation all necessary requirements to get the work done properly regardless of it's mentioned in the BoQ articles or not.
3 | In case that there is any item or detail in the drawings not mentioned in the BOQ (or vise versa) then this item or detail is considered included in the contractor's price for this project & he should execute it within his contract price without claiming any increase to the contract price, as it is considered part of the contract.
4 | All the BoQ articles must be carried out according to the guidelines of Sudanese Technical Specifications, with updates and instructions of IOM Engineer.
5 | All the BoQ articles comprise removing and transporting any debris or rubble to allocated disposal areas by municipality or local authority.
6 | The Contractor must obtain prior written approval from the IOM Programme Manager and the Procurement Unit for any cost-related Variation Orders. IOM Engineer will record and justify any variations to both parties. No VO shall be implemented without the Programme Manager's written approval.
7 | Site visit is required for vendor to see / inspect project, and to submit a letter mentioning site been visited with tendering documents.
8 | Follow IOM Engineer's instruction at all times.
9 | Submit work plan schedule for project activities.
Technical Specifications:
1 | The price includes all required materials, fittings , accessories , tools , machines , instruments, labor works with all the requirements, installing , testing and commissioning and put in operation to get the system work properly as per international specifications , beneficiary and IOM engineer instructions and to complete the works as stated in the contract items , shop drawings , details and complete the work in all aspects.
2 | Supplying of materials shall not be done before getting IOM Engineer's approval on the materials type, also the contractor should provide certificate of origin and tests result certificate for the supplied materials
3 | All materials should be a good quality and the brand and origin should be subject to the approval of IOM Engineer . Show sample for IOM Engineer's approval before installing. Cost include transportation and installation. Follow IOM Engineer's instruction during installation.
4 | Any damaged parts in any system or structure due to the work in the site , will be responsibility of contractor to redo poor workmanship without cost to IOM .
5 | Contractor / vendor is responsible to delivered all the works to local authority,beneficiary as well as IOM Engineer.
6 | Curing for all concrete works should be maintained 24 hours, the curing should be not less than 7 days before construction start on top any concrete structure
7 | Cleaning the site from any debris during and after complete all the work.
8 | The Contractor shall equip all materials, workers and equipment necessary for the performance of the work specified in the Bill of Quantities and Drowings in all its aspects.
9 | All Electrical connection shall be tested and commissioned before handover to IOM Engineer
10 | The company will be responsible for getting all approval of his documents from the government authorities in the State
11 | All the fees for materials transport handling and testing of samples should be paid by the Contractor if it mentioned in the BoQ or not.
12 | The Contractor implementing this project should hire laborers and workers from the locality as much as possible.
# | Description of Work | Unit | Quantity | Unit Rate USD | Amount USD | Remarks
1 | General
A | Mobilization and Demobilization
A.1 | Mobilization and demobilization of the contractor’s personnel, specialized equipment, tools, lifting devices, transport vehicles, and temporary facilities required for the execution of mechanical, civil, and electrical works under this contract. The item shall include transportation of pumps, motors, installation equipment, welding machines, generators, lifting cranes/chain blocks, testing instruments, and all related tools to and from the project site; establishment of temporary site facilities; provision of supervision and logistics; and final demobilization upon completion of the works. The rate shall also include removal of temporary structures, clearing of the site, and restoration of the work area to its original condition to the satisfaction of the Engineer | L.S | 1
B | Replacement of Air release valves
B.1 | Dismantle the existing DN50 air release valve full system and hand it over to SWC. Supply, install, test, and commission a new DN50 (2") Combination Air Release Valve (Triple Function), PN16, suitable for potable water transmission pipelines. The valve shall automatically release accumulated air during normal operation, discharge large volumes of air during pipeline filling, and admit large volumes of air during pipeline emptying or vacuum conditions. The work shall include all excavation, dewatering, backfilling, testing, reinstatement, and any necessary civil works. Valve Construction: -Nominal Size: DN50 (2") -Pressure Rating: PN16 -Body & Cover: Ductile Iron GGG50, epoxy coated -Float: Stainless Steel -Internal Trim: Stainless Steel -Seat Seal: EPDM -Coating: Fusion Bonded Epoxy -Flanged Ends: EN 1092-2 PN16 Complete Installation Includes: -DN50 isolation seated gate valve (PN16) -Flanges, gaskets, bolts, nuts, and washers -Reducer/branch connection from the existing main (DN300 to DN50) -Connecting pipe spool, fittings, welding/fabrication (where required), and all accessories for a complete installation, Hydrostatic/leak testing and commissioning. | No | 6
C | Replacement of DN300 HDPE Pipeline/fitting
C.1 | Remove and dispose of the existing damaged DN300 HDPE pipeline and install, test, and commission 30 m of HDPE pipe, DN300, PE100, SDR17, PN10, including all cutting, alignment, and butt fusion welding in accordance with the pipe manufacturer's recommendations. The work shall include supply and installation of two OD 315 HDPE stub ends complete with DN300 carbon steel/stainless steel backing rings, AISI 304 stainless steel bolts, nuts, washers for connection to the existing pipeline. The item shall also include excavation, dewatering (if required), sand bedding 15 cm at least, backfilling with approved material, compaction, cutting and removal of the existing pipe, pressure testing, reinstatement of all disturbed areas, all associated civil works, and coordination with SWC during shutdown and commissioning, complete in all respects; The pipe already exists and should not be priced. | L.S | 1
C.2 | Remove the damaged section and supply, install, test, and commission 2 m of HDPE pipe, DN300, PE100, SDR17, PN10, complete with butt fusion welding to the existing pipeline. The work shall include supply and installation of two OD 315 HDPE stub ends complete with DN300 carbon steel/stainless steel backing rings, AISI 304 stainless steel bolts, nuts, washers for connection to the existing pipeline, alignment, pressure testing, dewatering (if required), and all materials, equipment, labor, excavation, backfilling, compaction, reinstatement, and associated civil works necessary to fully restore the functionality of the main pipeline. The pipe already exists and should not be priced. | L.S | 1
C.3 | Repair the leaking DN300 HDPE pipeline by cutting and removing the damaged pipe section and installing a new two OD 315 HDPE stub ends complete with DN300 carbon steel/stainless steel backing rings, AISI 304 stainless steel bolts, nuts, washers for connection to the existing pipeline. The work shall include butt fusion welding where required, excavation, backfilling, dewatering (if required), compaction, pressure testing, reinstatement, and all associated civil works required to complete the repair and restore the pipeline to full operational condition. | L.S | 1
D | Rehabilitate the existing backwash system
D.1 | Carry out comprehensive rehabilitation of the existing backwash control valve DN 300 to restore it to full operational condition, including dismantling, inspection, replacement of the valve with similar brand, reassembly, testing, and commissioning. Decommission the existing backwash discharge arrangement through the inverted L-shaped outlet and modify the system by constructing a new 20 m long DN300 PE100 SDR17 PN10 HDPE discharge pipeline, connected to the valve outlet and laid with a continuous gravity slope toward the discharge point. The work shall include excavation, bedding, butt fusion welding, cutting, supply and installation of all required fittings, stub ends, backing rings, flanges, gaskets, stainless steel bolts and nuts, supports, backfilling, compaction, reinstatement, pressure testing, and all associated civil and mechanical works necessary to complete the installation. Coordinate all shutdown, testing, and commissioning activities with SWC. The pipe already exists and should not be priced. | L.S | 1
D.2 | Carry out complete backwashing of the entire 22 kW water transmission line to restore its hydraulic performance and remove accumulated sediments, debris, and deposits. The work shall include operation of the backwash system, controlled flushing until clean water is discharged, monitoring of flow rate and pressure, disposal of flushed water in an approved location, and all labor, equipment, tools, temporary connections, and consumables required to complete the operation. Coordinate all shutdown, flushing, testing, and recommissioning activities with SWC. Upon completion, verify that the pipeline is operating satisfactorily under normal service conditions. | L.S | 1
E | Chamber construction and concrete works
E.1 | Construct and rehabilitate the valve chamber for the DN300 control valve/ Air valve, with minimum internal dimensions of 1.50 m × 1.50 m × 1.50 m, using first-class fired red bricks and in accordance with the approved drawings and specifications. The work includes demolition and removal of the existing chamber, disposal of debris and unsuitable materials, excavation, dewatering, concrete base, brickwork, internal and external plastering, drainage, access steps, and proper sealing around pipe penetrations using approved waterstops or flexible sealants. The existing concrete cover shall be carefully removed, repaired, and reused on the new chamber. The cover shall be properly aligned and supported, including necessary surface repairs and lining. Existing lifting hooks shall be inspected and repaired or replaced where necessary;a new cover shall be fabricted simllar to the existing one where necessary. Provide a 650 × 650 mm manhole cover fitted with a 5 mm thick hot-dip galvanized steel cover and frame, complete with hinges, locking arrangement, fixing accessories, and required supports. The cover shall be reinforced with 1½-inch (40 mm) steel cross-bracing, 3 mm thick, to provide adequate strength and rigidity. The rate shall include all labour, materials, equipment, testing, reinstatement, and other works required to complete the chamber and leave it safe, functional, and ready for use, as directed by the Engineer | No | 7
G | Signboard
G.1 | Supply, fabrication, transportation, and installation of a project signboard comprising four (4) steel panels, each measuring 150 × 30 cm, mounted on a steel frame fabricated from 60 × 30 mm box section steel, 3 mm thick. The signboard panels shall be manufactured from 1.2 mm thick steel sheets, with a clear 80 mm gap between adjacent panels. The panels shall be fixed to steel support legs fabricated from 3-inch (75 MM) DIAMETER Circular steel pipe, 3 mm thick wall thickness, securely anchored into two (2) pits, each measuring 50 × 50 × 50 cm, using plain concrete (1:3:6 mix). The item shall include surface preparation, application of an anti-rust primer, and three coats of oil-based paint, finished with a white background and blue lettering, in accordance with the approved mock-up drawings and the directions of the IOM Engineer. The rate shall include all materials, accessories, labor, tools, equipment, transportation, and complete installation, fully finished and ready for use. | No | 1
TOTAL COST

## Rehab of tanks(Kumur, Gabas)
Bill of Quantities ( BOQ)
Project Name : Sudan Integrated Social Sector Infrastructure Rehabilitation Project (SISSIRP) Project Type : WASH Project Locations: Sennar , Jebal Moya Rehab of water tanks Project Duration: days
General Guidelines
1 | Drawings and BoQ are complementary to each other, hence the contractor has the obligation to execute the tasks mentioned in either one of them. Accordingly The contractor's shall include all what is mentioned in the drawings & all what is mentioned in the BOQs. Incase BOQ and technical drawings have discrepancies. BOQ supersedes technical drawings. Follow IOM site engineers site instruction at all times.
2 | All the BoQ articles comprise supplying manpower, machinery, equipment, transportation all necessary requirements to get the work done properly regardless of it's mentioned in the BoQ articles or not.
3 | In case that there is any item or detail in the drawings not mentioned in the BOQ (or vise versa) then this item or detail is considered included in the contractor's price for this project & he should execute it within his contract price without claiming any increase to the contract price, as it is considered part of the contract.
4 | All the BoQ articles must be carried out according to the guidelines of Sudanese Technical Specifications, with updates and instructions of IOM Engineer.
5 | All the BoQ articles comprise removing and transporting any debris or rubble to allocated disposal areas by municipality or local authority.
6 | The Contractor must obtain prior written approval from the IOM Programme Manager and the Procurement Unit for any cost-related Variation Orders. IOM Engineer will record and justify any variations to both parties. No VO shall be implemented without the Programme Manager's written approval.
7 | Site visit is required for vendor to see / inspect project, and to submit a letter mentioning site been visited with tendering documents.
8 | Follow IOM Engineer's instruction at all times.
9 | Submit work plan schedule for project activities.
Technical Specifications:
1 | The price includes all required materials, fittings , accessories , tools , machines , instruments, labor works with all the requirements, installing , testing and commissioning and put in operation to get the system work properly as per international specifications , beneficiary and IOM engineer instructions and to complete the works as stated in the contract items , shop drawings , details and complete the work in all aspects.
2 | Supplying of materials shall not be done before getting IOM Engineer's approval on the materials type, also the contractor should provide certificate of origin and tests result certificate for the supplied materials
3 | All materials should be a good quality and the brand and origin should be subject to the approval of IOM Engineer . Show sample for IOM Engineer's approval before installing. Cost include transportation and installation. Follow IOM Engineer's instruction during installation.
4 | Any damaged parts in any system or structure due to the work in the site , will be responsibility of contractor to redo poor workmanship without cost to IOM .
5 | Contractor / vendor is responsible to delivered all the works to local authority,beneficiary as well as IOM Engineer.
6 | Curing for all concrete works should be maintained 24 hours, the curing should be not less than 7 days before construction start on top any concrete structure
7 | Cleaning the site from any debris during and after complete all the work.
8 | The Contractor shall equip all materials, workers and equipment necessary for the performance of the work specified in the Bill of Quantities and Drowings in all its aspects.
9 | All Electrical connection shall be tested and commissioned before handover to IOM Engineer
10 | The company will be responsible for getting all approval of his documents from the government authorities in the State
11 | All the fees for materials transport handling and testing of samples should be paid by the Contractor if it mentioned in the BoQ or not.
12 | The Contractor implementing this project should hire laborers and workers from the locality as much as possible.
# | Description of Work | Unit | Quantity | Unit Rate USD | Amount USD | Remarks
1 | General
A | Mobilization and Demobilization
A.1 | Mobilization and demobilization of the contractor’s personnel, specialized equipment, tools, lifting devices, transport vehicles, and temporary facilities required for the execution of mechanical, civil, and electrical works under this contract. The item shall include transportation of pumps, motors, installation equipment, welding machines, generators, lifting cranes/chain blocks, testing instruments, and all related tools to and from the project site; establishment of temporary site facilities; provision of supervision and logistics; and final demobilization upon completion of the works. The rate shall also include removal of temporary structures, clearing of the site, and restoration of the work area to its original condition to the satisfaction of the Engineer. | L.S | 1
B | Rehabilitation of the elevated water tank, Booster Water pump / Kumur Alnayer
B.1 | Inspect, repair, rehabilitate and commission the existing elevated steel water tank and supporting tower, including all necessary labour, materials, equipment, testing and accessories, as follows: 1. Steel Tower Structural Rehabilitation Inspect and rehabilitate the existing steel tower, including repair or replacement of damaged, deformed or corroded structural members, bracing, connection plates and base plates. Inspect the anchor bolts and base-plate connections, particularly at the column bases, and replace damaged or severely corroded bolts, nuts and washers as required. Tighten and align loose connections and restore the structural stability of the tower in accordance with the approved requirements and SWC specifications. 2. Concrete Foundation Repairs Inspect concrete components using hammer test or equivalent methods to asses concrete durability, test is done to grade beams, pedestals, foundations, columns and other structural elements. Works shall include removal of loose concrete, treatment of exposed reinforcement and anchor bolts, crack repair using approved structural repair mortar or epoxy injection as appropriate, and reinstatement of damaged concrete with approved structural repair mortar/micro-concrete. Severely damaged sections shall be repaired or replaced as required. 3. Tank Shell/ base and Leakage Repair Inspect the tank internally and externally for all leakage points, corroded areas and damaged joints or panels/base. Repair leaking joints and welds, tighten or replace defective/corroded bolts, nuts and washers, replace damaged gaskets/sealing materials, and repair or replace severely corroded or perforated steel panels with suitable steel plates. Repair and seal pipe penetrations, flanges and other fittings where required. Carry out a water-tightness test after completion. 4. Internal and External Tank Coating Prepare the internal tank surfaces by removing rust, scale, loose coating and contaminants. Apply an approved anti-corrosion primer followed by two coats of certified potable-water-grade epoxy lining, suitable for contact with drinking water, in accordance with the manufacturer's requirements. Prepare the external tank surfaces and apply two coats of approved anti-corrosion primer and one durable weather-resistant finishing coat, including all necessary touch-up works. 5. Tower Cleaning and Painting Clean and prepare the complete steel tower, including columns, bracing and connections, removing rust, loose paint and contaminants. Apply two coats of approved anti-corrosion primer and one final weather-resistant finishing coat. 6. Valves and Pipework Replace the existing two 3-inch pn 16 and 2 inch pn 10 isolation gate valves, complete with, gaskets, bolts, nuts, washers, and other accessories, and connect to the existing pipework. Repair sockets, flanges, gaskets and replace stainless-steel bolts as required, including all associated fittings and accessories 7. Overflow Valve/Manhole and Fittings Repair or replace the existing overflow valve/manhole cover, sockets, flanges, gaskets and stainless-steel bolts as required, including all associated fittings and accessories. 8. Access Ladder Safety Protection Repair the ladder to restore the functionality and fabricate and install a circular safety protection cage around the access ladder using 16 mm diameter steel bars and hoops, commencing approximately 2 m above ground level, including fixing, welding, corrosion protection and painting, in accordance with the approved drawings and safety requirements. 9. Internal Bracing Inspect all internal bracing members for corrosion, deformation, cracks and loose or missing connections. Replace damaged or severely corroded bracing members where required, including corroded or missing bolts, nuts and washers. Reinstate and secure all connections and apply suitable corrosion protection in accordance with SWC specifications. 10. Cleaning, Disinfection and Final Testing Upon completion, thoroughly clean and wash the tank, disinfect it using an approved potable-water disinfection procedure, and carry out final watertightness, leakage and operational tests to confirm that the tank is safe, watertight and fully operational. | Job | 1
B.2 | Construction of Water Distribution Stand Construct a water distribution stand measuring approximately 3.0 m long × 0.8 m high × 0.6 m deep, using good-quality first-class bricks. Apply cement mortar plaster using a 1:6 cement-to-sand mix, with SBR bonding/admixture at 2 litres per 50 kg cement bag, in accordance with the manufacturer's recommendations. 2. Concrete Slab and Drainage Excavate an area of 6.0 m × 3.0 m × 200 mm deep and backfill with 150 mm of approved selected material, compacted mechanically in suitable layers. Construct a 6.0 m × 3.0 m × 150 mm reinforced concrete slab using 1:2:4 concrete mix, reinforced with 12 mm diameter steel bars at 150 mm spacing in both directions. Provide a suitable slope to ensure positive drainage away from the distribution point to the landscape tress and connect the slab to the surrounding ground to prevent water ponding. 3. Galvanized Steel Pipework • Supply and install approximately 5 m of 3-inch galvanized steel pipe connected to the distribution stand, including all required fittings and accessories include 3 inch gate valve PN10. • Supply and install approximately 20 m of 3-inch galvanized steel pipe from the tank discharge, including all required fittings and accessories. • Buried pipework shall be installed at approximately 300 mm below ground level, including excavation and backfilling. • Galvanized/metallic pipework shall be cleaned and protected with two coats of approved anti-corrosion paint. 4. Service Outlets and Hoses Provide two service outlets, each complete with: • Connection from the 3-inch main through a 3-inch × 2-inch tee; • Required cutting, threading and connection works; • 2-inch full-bore ball valve with lever handle; • 10 m long, 2-inch flexible hose; • Hose couplings/connectors, nozzles and stainless-steel clamps; • All required fittings and accessories. Provide suitable galvanized wall-mounted hose hangers/brackets to keep the hoses elevated and prevent contact with the ground when not in use. 5. Excavation, Backfilling and Testing The scope shall include all necessary excavation, selected-material filling, mechanical compaction, backfilling, concrete works, pipe supports, fittings, accessories, pressure/leakage testing and commissioning required to provide a complete and operational installation. | Job | 1
B.3 | Supply, transport, and plant Four (4) trees at the Distribution Point , including site preparation, setting out, excavation of planting pits measuring 600 mm × 600 mm × 1,000 mm deep, backfilling with approved fertile topsoil mixed with organic fertilizer, planting of healthy nursery-grown trees, initial watering, staking where required, mulching, and all necessary materials, labor, tools, and equipment. The contractor shall maintain the trees during the establishment period, including regular watering and replacement of any trees that fail to survive, to ensure healthy growth and successful establishment. to be assessed during the site visit. | No | 4
B.4 | Dismantle the old room and hand over the materials to SWC in the presence of IOM and community and backfill the pump chamber; Construction of a pump room, including the supply of all materials, labour, equipment, and services required to complete the works in accordance with the approved technical drawings and specifications. The pump room shall have internal dimensions of 3.5 × 3.5 × 3.0 m. The structural frame shall be fabricated from 2.5-inch steel angle sections with a minimum thickness of 5 mm. Roof and wall purlins shall be constructed using 2-inch steel angles with a minimum thickness of 3 mm, installed at 800 mm centre-to-centre spacing. The walls and roof shall be fully clad with Grade 35 galvanized steel zinc sheets of standard profile. The foundation and floor shall consist of plain in-situ concrete footings and floor slab, constructed in accordance with the approved structural drawings. The pump room shall be provided with: One steel door fitted with a 93 mm heavy-duty padlock, including internal and external deadbolts. Two steel-framed windows. Window protection grills fabricated from 12 mm diameter steel reinforcement bars. Finishes: All steel components, including the structural frame, purlins, doors, windows, and grills, shall be coated with anti-rust primer and finished with two coats of exterior-grade enamel paint, colour as directed by the Engineer. Provision shall also be made for cable glands and protective conduits for the main submersible pump power cable and control wiring, installed at the base of the wall adjacent to the borehole discharge head. All works shall be executed in full compliance with the specifications, drawings, and requirements outlined in the tender documents. | Job | 1
B.5 | Dismantle the old pump set and hand over the materials to SWC in the presence of IOM and community; Supply, install, test, and commission one horizontal end-suction centrifugal pump complete with a 10 HP (7.5 kW), IE3, TEFC, 3-phase, 400/415 V, 50 Hz, 2-pole electric motor, suitable for a duty point of 50 m³/h at 30 m total dynamic head. The pump shall have DN100 suction × DN80 discharge connections. The pump casing shall be cast iron, while the impeller and shaft shall be stainless steel. The Contractor shall submit the manufacturer's certified pump performance (Q-H) curve, clearly indicating the specified duty point, together with the technical data sheet for approval prior to installation. The scope of work shall include connection of the pump to the existing 110 mm HDPE pipeline, including all necessary fittings and accessories such as HDPE adaptors with stub flanges and backing rings, DN100 tee and elbows, DN100 × DN80 flanged reducer from stainless steel two DN100 flanged gate valves, bolts, nuts, washers, and gaskets. The work shall also include installation of a bypass line using PE100 PN10 SDR17 HDPE pipe with all required fittings and PN 10 gate valves, elbows, tees, adapters and stub flanges, bolts and nuts, washers. All pipework shall be adequately supported on H-beam steel sections (120 mm), complete with support, anchors bolts, and fasteners the HDPE components shall be connected using but fusion.; and the rate includes associated civil work. Mounting: Supply, cast, and cure a reinforced concrete foundation of minimum C25/30 concrete. Foundation dimensions shall be based on the pump manufacturer's certified foundation drawing, with sufficient projection beyond the base frame on all sides. Foundation thickness shall be approximately 300 mm. Approved brand: Algo, Pentax, or equivalent, The pump shall be protected by a fabricated galvanized-mesh cage made from 1.5-inch angle bar with 3 mm thickness. The cage shall include diagonal internal bracing for additional strength and shall securely ancho bolts 4 at each foot in base plate of 20*20 cm and 5mm thickness. The cage shall be painted with two coats of anti-rust primer followed by a final oil-based paint coat. A suitable clearance shall be maintained between the cage and control box to provide adequate access, ventilation, and working space for future inspection, maintenance, and repair. The cage shall be fitted with a high-quality lock and all necessary fixing and accessories. | Job | 1
B.6 | AC Control Panel (Pump Room) Supply and installation of AC control panel/ box for 7.5 kW motor including: 32A MCCB (ABB or approved equivalent) Contactor Rating: Minimum 25 A (AC-3 category), Coil Voltage: 220–240 V AC and 3-Pole Thermal overload relay 13–18 A adjustable Phase failure & phase sequence relay, Rated for 380–415 V, 3-phase, Protection against: Phase loss, Phase reversal; Under/over voltage. Start/Stop push buttons Ammeter and voltmeter Panel box shall be: IP54 minimum; Lockable; Corrosion-resistant Mounted securely in pump room; Rate includes supply and installation of Two Condensed Hot Aerosol Fire Extinguishing Device with the following specifications: Approved brand: QRRO.01G/SCFLC Operating temperature: −50°C to +90°C Service life: 10 years Extinguishing Density:100 g/m3 Surface temperature of Casing 200 C Oxidizer: SR(NO), 60 %/ KNO 20%. | No | 1
B.7 | Supply, lay, test, and commission 65 m of 4-core × 6 mm² copper conductor, XLPE insulated, SWA , PVC sheathed, 0.6/1 kV power cable, suitable for direct underground burial, for connection of the 7.5 kW (10 HP), 3-phase, 400/415 V, 50 Hz pump motor, complete in all respects; fully compatible with the submersible pump of 2 * 3P MCCB 100 A with boxes Andeli/ Havells / ABB / or equivalent approved brand. The scope shall include excavation of the cable trench to the minimum depth of 70 cm and, a 10 cm sand bedding below and above the cable, installation of the cable, protective cable bricks, warning tape, selected backfilling and compaction, cable identification markers, compression glands, cable lugs brass, terminations at both ends, supports where required, testing, commissioning, and all accessories necessary for a complete and operational installation. The Contractor shall coordinate with the Electrical Distribution Company and obtain all required permits, approvals, and clearances necessary for the execution. | Ml | 65
C | Rehabilitation of the elevated water tank, Jabal Moya 1
C.1 | Inspect, repair, rehabilitate and commission the existing elevated steel water tank and supporting tower, including all necessary labour, materials, equipment, testing and accessories, as follows: 1. Steel Tower Structural Rehabilitation Inspect and rehabilitate the existing steel tower, including repair or replacement of damaged, deformed or corroded structural members, bracing, connection plates and base plates. Inspect the anchor bolts and base-plate connections, particularly at the column bases, and replace damaged or severely corroded bolts, nuts and washers as required. Tighten and align loose connections and restore the structural stability of the tower in accordance with the approved requirements and SWC specifications. 2. Concrete Foundation Repairs Inspect concrete components using hammer test or equivalent methods to asses concrete durability, test is done to grade beams, pedestals, foundations, columns and other structural elements. Works shall include removal of loose concrete, treatment of exposed reinforcement and anchor bolts, crack repair using approved structural repair mortar or epoxy injection as appropriate, and reinstatement of damaged concrete with approved structural repair mortar/micro-concrete. Severely damaged sections shall be repaired or replaced as required 3. Tank Shell and Leakage Repair Inspect the tank internally and externally for all leakage points, corroded areas and damaged joints or panels. Repair leaking joints and welds, tighten or replace defective/corroded bolts, nuts and washers, replace damaged gaskets/sealing materials, and repair or replace severely corroded or perforated steel panels with suitable steel plates. Repair and seal pipe penetrations, flanges and other fittings where required. Carry out a water-tightness test after completion. 4. Internal and External Tank Coating Prepare the internal tank surfaces by removing rust, scale, loose coating and contaminants. Apply an approved anti-corrosion primer followed by two coats of certified potable-water-grade epoxy lining, suitable for contact with drinking water, in accordance with the manufacturer's requirements. Prepare the external tank surfaces and apply two coats of approved anti-corrosion primer and one durable weather-resistant finishing coat, including all necessary touch-up works. 5. Tower Cleaning and Painting Clean and prepare the complete steel tower, including columns, bracing and connections, removing rust, loose paint and contaminants. Apply two coats of approved anti-corrosion primer and one final weather-resistant finishing coat. 6. Valves and Pipework Replace the existing one 3-inch isolation gate valves, complete with, gaskets, bolts, nuts, washers, and other accessories, and connect to the existing pipework. 7. Overflow Valve/Manhole and Fittings Repair or replace the existing overflow valve/manhole cover, sockets, flanges, gaskets and stainless-steel bolts as required, including all associated fittings and accessories. 8. Access Ladder Safety Protection Repair the ladder to restore the functionality and fabricate and install a circular safety protection cage around the access ladder using 16 mm diameter steel bars and hoops, commencing approximately 2 m above ground level, including fixing, welding, corrosion protection and painting, in accordance with the approved drawings and safety requirements. 9. Internal Bracing Inspect all internal bracing members for corrosion, deformation, cracks and loose or missing connections. Replace damaged or severely corroded bracing members where required, including corroded or missing bolts, nuts and washers. Reinstate and secure all connections and apply suitable corrosion protection in accordance with SWC specifications. 10. Cleaning, Disinfection and Final Testing Upon completion, thoroughly clean and wash the tank, disinfect it using an approved potable-water disinfection procedure, and carry out final watertightness, leakage and operational tests to confirm that the tank is safe, watertight and fully operational. | Job | 1
C.2 | Excavation, sand bedding with clean, coarse, well-graded sand of at least 100 mm, and backfilling of trenches for OD 110 mm PN10 HDPE pipes in any material other than rock, to a depth of 0.6 m / Same depth of the exisit pipe, Includes compliance with all safety regulations regarding trench support, provision of necessary shoring, planking, and trench safety systems. | Ml | 10
C.3 | Supply, installation, laying, jointing, testing, and commissioning of 110 mm HDPE pipes (PE100, PN10, SDR17) per linear meter, including proper jointing by butt fusion welding . Unit rate to include all labour, materials, equipment, supervision, and incidental works required for completion. | Ml | 10
C.4 | Supply, installation of OD 110 stub flange complete with DN 100 backing ring, nuts and bolts & gaskets | No | 3
C.5 | Supply, install, test, and commission one horizontal end-suction centrifugal pump complete with a 10 HP (7.5 kW), IE3, TEFC, 3-phase, 400/415 V, 50 Hz, 2-pole electric motor, suitable for a duty point of 50 m³/h at 30 m total dynamic head. The pump shall have DN100 suction × DN80 discharge connections. The pump casing shall be cast iron, while the impeller and shaft shall be stainless steel. The Contractor shall submit the manufacturer's certified pump performance (Q-H) curve, clearly indicating the specified duty point, together with the technical data sheet for approval prior to installation. The scope of work shall include connection of the pump to the existing 110 mm HDPE pipeline, including all necessary fittings and accessories such as HDPE adaptors with stub flanges and backing rings, DN100 elbows, DN100 × DN80 flanged reducer from stainless steel one isolation DN100 flanged gate valves, bolts, nuts, washers, and gaskets. The work shall also include installation of a bypass line to the distribution point using DN 50 PE100 PN10 SDR17 HDPE pipe with all required fittings flanged DN 50 PN10 Valve and NRV DN50 PN 10. Install before the DN 100 valve. All pipework shall be adequately supported on H-beam steel sections (120 mm) embedded in the concrete, complete with support, anchors, and fasteners the HDPE components shall be connected using but fusion.; and the rate includes associated civil work. Mounting: Supply, cast, and cure a reinforced concrete foundation of minimum C25/30 concrete. Foundation dimensions shall be based on the pump manufacturer's certified foundation drawing, with sufficient projection beyond the base frame on all sides. Foundation thickness shall be approximately 300 mm. Approved brand: Algo, Pentax, or equivalent The price shall include the complete connection of the motor to the control panel using 4-core, 6 mm² flat copper cable, including all necessary cable glands, lugs, termination accessories, supports, and fittings. | Job | 1
C.6 | AC Control Panel (Pump Room) Supply and installation of AC control panel/ box for 7.5 kW motor including: 32A MCCB (ABB or approved equivalent) Contactor Rating: Minimum 25 A (AC-3 category), Coil Voltage: 220–240 V AC and 3-Pole Thermal overload relay 13–18 A adjustable Phase failure & phase sequence relay, Rated for 380–415 V, 3-phase, Protection against: Phase loss, Phase reversal; Under/over voltage. Start/Stop push buttons Ammeter and voltmeter Panel box shall be: IP54 minimum; Lockable; Corrosion-resistant Mounted securely in selected room; Rate includes supply and installation of Two Condensed Hot Aerosol Fire Extinguishing Device with the following specifications: Approved brand: QRRO.01G/SCFLC Operating temperature: −50°C to +90°C Service life: 10 years Extinguishing Density:100 g/m3 Surface temperature of Casing 200 C Oxidizer: SR(NO), 60 %/ KNO 20%. | No | 1
C.7 | Supply, lay, test, and commission 50m of 4-core × 6 mm² copper conductor, XLPE insulated, SWA , PVC sheathed, 0.6/1 kV power cable, suitable for direct underground burial, for connection of the 7.5 kW (10 HP), 3-phase, 400/415 V, 50 Hz pump motor, complete in all respects; fully compatible with the submersible pump of 2 * 3P MCCB 100 A with boxes Andeli/ Havells / ABB / or equivalent approved brand. The scope shall include excavation of the cable trench to the Minimum depth of 70 cm and, a 100 mm sand bedding below and above the cable, installation of the cable, protective cable bricks, warning tape, selected backfilling and compaction, cable identification markers, compression glands, cable lugs brass, terminations at both ends, supports where required, testing, commissioning, and all accessories necessary for a complete and operational installation. The Contractor shall coordinate with the Electrical Distribution Company and obtain all required permits, approvals, and clearances necessary for the execution. | Ml | 20
C.8 | Construction of a pump room, including the supply of all materials, labour, equipment, and services required to complete the works in accordance with the approved technical drawings and specifications. The pump room shall have internal dimensions of 3.5 × 3.5 × 3.0 m. The structural frame shall be fabricated from 2.5-inch steel angle sections with a minimum thickness of 5 mm. Roof and wall purlins shall be constructed using 2-inch steel angles with a minimum thickness of 3 mm, installed at 800 mm centre-to-centre spacing. The walls and roof shall be fully clad with Grade 35 galvanized steel zinc sheets of standard profile. The foundation and floor shall consist of plain in-situ concrete footings and floor slab, constructed in accordance with the approved structural drawings. The pump room shall be provided with: One steel door fitted with a 93 mm heavy-duty padlock, including internal and external deadbolts. Two steel-framed windows. Window protection grills fabricated from 12 mm diameter steel reinforcement bars. Finishes: All steel components, including the structural frame, purlins, doors, windows, and grills, shall be coated with anti-rust primer and finished with two coats of exterior-grade enamel paint, colour as directed by the Engineer. Provision shall also be made for cable glands and protective conduits for the main submersible pump power cable and control wiring, installed at the base of the wall adjacent to the borehole discharge head. All works shall be executed in full compliance with the specifications, drawings, and requirements outlined in the tender documents. | Ls | 1
C.9 | Rehabilitation of Water Distribution Stand Rehabilitate the existing water distribution stand, approximately 3.0 m long × 0.8 m high × 0.6 m deep, including removal of the existing damaged plaster, cleaning and preparation of the surface, and application of new cement mortar plaster using a 1:6 cement-to-sand mix. Add SBR bonding/admixture at 2 litres per 50 kg cement bag, in accordance with the manufacturer's recommendations. 2. Concrete Slab and Drainage Construct a 5.0 m × 3.0 m × 100 mm reinforced concrete slab using 1:2:4 concrete mix, reinforced with 12 mm diameter steel bars at 150 mm spacing in both directions. The slab shall be finished with an adequate slope for positive drainage away from the distribution point and connected to the surrounding landscape trees to prevent water ponding. Approximately 4.0 m of the slab shall extend in front of the distribution point. 3. Galvanized Pipe Replacement • Replace approximately 5 m of 3-inch galvanized steel pipe connected to the distribution point, including all required fittings and accessories and connect the point with bypass line from the pump using tee and reducer 3 inch * 2 inch and DN 50 flangged valve pn 10. • Replace approximately 14 m of 3-inch galvanized steel pipe from the tank discharge, including repair or replacement of rusted sections and all necessary fittings. • Retain the existing saddle where it is in good condition and connect it using a 3-inch × 1-inch tee. The connection/pipeline shall be buried approximately 300 mm below ground level, with exposed steel surfaces protected with two coats of anti-corrosion paint. 4. Service Outlets and Hoses Provide two service outlets, each complete with: • 2-inch full-bore ball valve with lever handle; • 10 m long, 2-inch flexible hose; • Hose couplings/connectors, nozzles and stainless-steel clamps; • Saddle and all required fittings. Provide suitable wall-mounted galvanized hose hangers/brackets to keep the hoses elevated and prevent contact with the ground when not in use. 5. Excavation, Backfilling and Testing The works shall include all necessary excavation, backfilling, concrete works, pipe fittings, supports, accessories, pressure/leakage testing and commissioning required to provide a complete and operational installation. | Job | 1
C.10 | Supply, transport, and plant five (5) trees at the Distribution Point , including site preparation, setting out, excavation of planting pits measuring 600 mm × 600 mm × 1,000 mm deep, backfilling with approved fertile topsoil mixed with organic fertilizer, planting of healthy nursery-grown trees, initial watering, staking where required, mulching, and all necessary materials, labor, tools, and equipment. The contractor shall maintain the trees during the establishment period, including regular watering and replacement of any trees that fail to survive, to ensure healthy growth and successful establishment. to be assessed during the site visit. | No | 5
C.11 | Construction of a complete chain-link perimeter fence, including the supply of all materials, labour, tools, equipment, and services necessary to execute and complete the works in accordance with the approved technical drawings and tender specifications. General Specifications • Total fence height: 2.0 metres, Additional 0.5 metres razor wire topping, Total overall height: 2.5 metres Structural Framework • Vertical posts: 2 inch angle bar at least 3 mm thickness, Post spacing: 2.0 metres centre-to-centre, Posts to be securely anchored in lean concrete footings as per drawings. Chain-Link Mesh Installation • Galvanized chain-link mesh fixed to the steel frame. • Horizontal reinforcement using: 10 mm steel rebars at top, middle, and bottom o 3 mm iron binding wire for secure fastening Razor Wire Topping • Razor wire with a minimum diameter of 50 cm, Installed continuously along the fence top in V shape, Fixed using iron angles and steel bars to ensure stability and security As per approved drawings Double-Leaf Access Gate Provision of one double-leaf steel gate fabricated as follows: As per approved drawingss • Main frame: 2 inchs angle bar 5 mm thickness and one inch angle bar, Footing depth: 80 cm minimum, Footing dimensions: As per approved drawingss) • Fitted with: o Four (4) heavy-duty hinges Drop bolts with holders o Lock provision with padlock 93-95 mm o All necessary accessories for smooth and secure operation Finishing • All steel components shall be: o Cleaned and prepared, Two coat of primer, Two coats of anti-rust paint, Two coats of approved enamel paint finish All works shall be executed strictly in accordance with the approved drawings, technical specifications, and conditions outlined in the tender documentation. | ML | 60
C.12 | Supply and installation of one (1) trolley-mounted CO₂ (Carbon Dioxide) fire extinguishers, each with a 30 kg capacity, suitable for extinguishing Class B fires and fires involving energized electrical equipment, including all necessary accessories and a robust wheeled trolley. The extinguishers shall be brand new, fully charged, certified, and suitable for energized electrical equipment, with the applicable fire classification and certification clearly marked on each unit. Each unit shall include a suitable discharge hose/horn, safety pin, tamper seal, operating valve and trolley, and shall comply with applicable BS EN 1866-1 or equivalent requirements. The Contractor shall provide basic operational training to the pump operator on the safe and correct use of CO₂ fire extinguishers. Training shall be conducted using a separate extinguisher designated for training purposes and shall not involve discharging the installed units. | No | 1
D | Rehabilitation of the elevated water tank, Jabal Moya/ Gabas
D.1 | Rehabilitate the existing 10 m × 10 m × 3 m deep reinforced-concrete ground water tank, including all necessary labour, materials, fittings, testing and commissioning. 1. Cleaning and Desilting Thoroughly clean the tank and remove all accumulated sludge, mud, sediment, water, waste and other materials. Dispose of the removed materials at an approved location. Repair the existing manhole base as required and provide a new 600 × 600 mm manhole cover. 2. External Concrete Repair and Plastering Repair loose and deteriorated concrete surfaces (Walls and top slab) and prepare them for plastering. Apply new cement mortar plaster for he external walls using a 1:8 cement-to-sand mix, with SBR admixture at 2 litres per 50 kg cement bag; The plastering area is approximately 1.1 m high × 40 m long. 3. Internal Concrete Repair and Waterproofing Inspect and repair cracks, honeycombing and other defective concrete surfaces before applying the waterproofing system. After proper surface preparation, apply an approved, certified potable-water-grade waterproofing system to the internal tank surfaces. The system shall be suitable for direct contact with drinking water and applied according to the manufacturer's recommendations. 4. Supply Pipeline Modification Modify the existing 160 mm (6-inch) supply pipeline at the metallic section after the existing valve, including cutting and removing the existing welded elbow as required and installing a new 6-inch stub flange. Replace approximately 7 m of the existing metallic pipe with 160 mm PE100, PN10, SDR17 HDPE pipe, including all required fittings, stub ends, flange adaptors, backing rings, bolts, gaskets and accessories. Replace the existing DN150 PN10 valve with a new valve of the same size, complete with all required connections and fittings. The HDPE pipeline was buried to a maximum depth of 1.0 m, including excavation, bedding, backfilling and reinstatement. Test and commission the completed pipeline. The remaining exposed metallic pipework shall be cleaned and painted with two coats of approved anti-corrosion primer and one final protective coat. 5. Vent Protection Supply and install suitable 4-inch caps for five (5) existing tank vents, including all required fittings and fixing accessories, while maintaining adequate ventilation and preventing the entry of dust, insects and other contaminants. 6. Final Cleaning and Testing Upon completion, thoroughly clean and wash the tank, remove all construction materials and debris, and carry out the required water-tightness, leakage and pipeline pressure tests. | Job | 1
D.2 | Chamber construction and concrete works: Construction of valve chamber using Fired red bricks first class block masonry, in accordance with approved drawings and specifications, suitable for 200 mm, 150 mm, and 100 mm control valves, minimum internal dimensions 1.50 m × 1.50 m × 1.20 m. Includes excavation, disposal, backfilling and compaction; reinforced concrete works; block masonry; internal and external plastering; drainage provisions; access steps; waterstop installation or flexible sealant boots/styrofoam at wall penetrations; finishing works. Chamber fitted with galvanized steel chequered plate cover with lockable hinges, complete and operational. Rate to include all labour, materials, equipment, and incidentals, complying with applicable international standards and UN technical requirements. | No | 1
D.3 | Supply, install, test and commission one horizontal end-suction centrifugal pump complete with a 10 HP (7.5 kW), IE3, TEFC, 3-phase, 400/415 V, 50 Hz, 2-pole motor, suitable for a duty point of 50 m³/h at 30 m total dynamic head (TDH). The pump shall have DN100 suction × DN80 discharge connections, cast-iron casing, and stainless-steel impeller and shaft. The Contractor shall submit the manufacturer's certified Q-H performance curve, clearly showing the specified duty point, together with the pump technical data sheet for approval before installation, connect the pump motor using 4 C× 4 mm² copper flexible rubber-insulated flat cable, suitable for 3-phase, 380/415 V, 50 Hz supply, with the required cable length from the motor to the pump control panel. Pump Foundation: Provide a reinforced concrete foundation using minimum C25/30 concrete, with dimensions based on the manufacturer's approved foundation drawing and sufficient projection beyond the pump base frame. Foundation thickness shall be approximately 300 mm, unless otherwise specified by the manufacturer. Suction Pipework: supply and install 110 mm PE100 PN10 SDR17 HDPE suction pipe from the ground tank to the pump, including all required fittings, flange adaptors and supports. Provide suitable H-beam supports securely fixed to the existing structure. Install a 4-inch stainless-steel foot valve with integrated strainer inside the tank, positioned above the tank floor by 25 cm. Modify the existing tank pipe penetration to suit the new HDPE pipe, including the required sleeve/flange connection and a watertight potable-water-approved seal. Priming Arrangement: Provide a 2-inch HDPE priming connection on the pump suction side, complete with DN50 PN10 isolation valve and DN50 PN10 NRV, connection will be from the ground tank inlet. Delivery Pipework: Supply and install approximately 95 m of 110 mm PE100 PN10 SDR17 HDPE delivery pipe, buried at approximately 800 mm depth, including 100 mm sand bedding, excavation, backfilling and reinstatement. Provide: • DN100 PN10 isolation valve; • DN100 PN10 flanged non-return valve (NRV); • DN100 × DN80 reducer at the pump discharge; • DN100 × DN80 reducer at the tank riser; • All required stub ends, flange adaptors, backing rings, bolts, nuts, gaskets and other fittings. Testing and Commissioning: Test the complete suction and delivery pipework for leakage and pressure, flush the system, and commission the pump to confirm operation at the specified 50 m³/h at 30 m TDH duty point. The Contractor shall ensure that the pump maintains prime and operates without excessive vibration, leakage or abnormal noise. Approved brand: Algo, Pentax, or equivalent | Job | 1
D.4 | Supply, installation, testing, and commissioning of solar photovoltaic modules with: Total Array Capacity: ≥ 12 kWp Individual Panel Rating: 710 W or 720 W 17 A Suitable to operate 7.5 kW, 3-phase, 415 V, 50 Hz pump motor Approved manufacturers: LONGi Green Energy Technology (HI-MO series) / Trina Solar / or approved equivalent. All modules shall: Comply with IEC 61215 & IEC 61730 Be PID resistant Include factory warranty certificates, The Contractor shall provide basic operational training to the pump operator on the correct use of the system and troubleshooting of the solar power system. | Set | 1
D.5 | Design, supply, and installation of steel mounting structure: Orientation: True South-facing Tilt angle: 15° Wind load resistance: ≥ 40 m/s Front leg height: 1 m above ground Mounted on reinforced concrete foundations (as per drawings) Surface treatment: One anti-rust primer coat One final enamel coat All works shall comply with structural drawings and specifications. | Job | 1
D.6 | Supply, installation, and commissioning of solar pump inverter with: Built-in MPPT controller Integrated VFD (Variable Frequency Drive) Soft starter functionality 3-phase 380–415 V output Rated capacity ≥ 10 kW Max. DC input voltage at least 900 V IP65 weatherproof metallic enclosure Approved brands: Lorentz / JNTECH / or equivalent. Inverter shall: Convert DC from PV array to AC for pump motor Operate under low solar radiation Include dry-run, overload, over/under voltage, and phase protection. | Set | 1
D.7 | DC/ AC Protection (Per PV String) with all necessary fixing and accessories. Each PV string shall include: 2 × 25A cylindrical DC fuses (10×38 mm, 1000V DC rated) 1 × 32A, 2-pole DC MCB (1000V DC rated) Surge protection devices and connected with the earthing systems protection MCB/fuse Start/Stop push buttons 32A MCCB (ABB or approved equivalent) 3P, to be installed at the VFD output. 2 × Passive cooling with ventilation fans. 2 × Condensed Hot Aerosol Fire Extinguishing Device with the following specifications: Approved brand: QRRO.01G/SCFLC Operating temperature: −50°C to +90°C Service life: 10 years Extinguishing Density:100 g/m3 Surface temperature of Casing 200 C Oxidizer: SR(NO), 60 %/ KNO 20%. Panel box Panel box shall be: Supply and install an IP65, lockable, corrosion-resistant control box, securely mounted under the solar structure at a suitable height above ground. The control box shall be protected by a fabricated galvanized-mesh cage made from 1.5-inch angle bar with 3 mm thickness. The cage shall include diagonal internal bracing for additional strength and shall be securely anchored to concrete blocks measuring approximately 20 × 20 × 30 cm deep. The cage shall be painted with two coats of anti-rust primer followed by a final oil-based paint coat. A suitable clearance shall be maintained between the cage and control box to provide adequate access, ventilation, and working space for future inspection, maintenance, and repair. The cage shall be fitted with a high-quality lock 95 mm and all necessary fixing and accessories. | Set | 1
D.8 | Supply and installation of: • 6 mm² single-core solar DC cable (H1Z2Z2-K, 1500V rated, red & black) Installation requirements: • Cables shall be installed in sufficient lengths to ensure proper interconnection between the solar PV array and the solar PV controller. The rate shall include all necessary accessories. • Buried in 2-inch heavy-duty PPR conduit at ≥ 30 cm depth • Installed in flexible UV-resistant conduits within panels frame includes all hinges and accessories. • Installed in heavy duty concrete pipes conduits within panels frame includes all hinges and accessories. • Including civil work, trenching, backfilling, and pipe fittings All work shall comply with relevant IS and IEC standards and shall conform to the technical specifications outlined in Annex. | ML | 60
D.9 | Supply, installation, and testing of a complete earthing and lightning protection system for the solar PV and pump system. Conduct soil resistivity survey and the earthing system shall ensure an earth resistance ≤ 5 Ω, measured after installation and commissioning. Lightning protection shall include air terminals (isolated air terminals), down conductors typically copper , and earth termination, fully integrated with the earthing system to protect all PV and pump electrical components. All conductors, electrodes, and accessories shall be sized and installed in accordance with the tender technical specifications, international standards, and best engineering practice. The contractor shall carry out all necessary testing and commissioning, including earth resistance measurements, continuity checks, and visual inspections, and submit a test report for approval. | L.S | 1
D.10 | Construct an embankment measuring using approved selected fill material. The fill shall be placed in uniform layers not exceeding 200 mm in thickness and compacted mechanically. The work shall include site preparation, dewaterig hauling, spreading, moisture conditioning, compaction, trimming to the required levels and slopes. | M3 | 100
D.11 | Construction of a complete chain-link perimeter fence, including the supply of all materials, labour, tools, equipment, and services necessary to execute and complete the works in accordance with the approved technical drawings and tender specifications. General Specifications • Total fence height: 2.0 metres, Additional 0.5 metres razor wire topping, Total overall height: 2.5 metres Structural Framework • Vertical posts: 2 inch angle bar at least 3 mm thickness, Post spacing: 2.0 metres centre-to-centre, Posts to be securely anchored in lean concrete footings as per drawings. Chain-Link Mesh Installation • Galvanized chain-link mesh fixed to the steel frame. • Horizontal reinforcement using: 10 mm steel rebars at top, middle, and bottom o 3 mm iron binding wire for secure fastening Razor Wire Topping • Razor wire with a minimum diameter of 50 cm, Installed continuously along the fence top in V shape, Fixed using iron angles and steel bars to ensure stability and security As per approved drawings Double-Leaf Access Gate Provision of one double-leaf steel gate fabricated as follows: As per approved drawingss • Main frame: 2 inchs angle bar 5 mm thickness and one inch angle bar, Footing depth: 80 cm minimum, Footing dimensions: As per approved drawingss) • Fitted with: o Four (4) heavy-duty hinges Drop bolts with holders o Lock provision with padlock 93-95 mm o All necessary accessories for smooth and secure operation Finishing • All steel components shall be: o Cleaned and prepared, Two coat of primer, Two coats of anti-rust paint, Two coats of approved enamel paint finish All works shall be executed strictly in accordance with the approved drawings, technical specifications, and conditions outlined in the tender documentation. | ML | 80
D.12 | Inspect, repair, rehabilitate and commission the existing elevated steel water tank and supporting tower, including all necessary labour, materials, equipment, testing and accessories, as follows: 1. Steel Tower Structural Rehabilitation Inspect and rehabilitate the existing steel tower, including repair or replacement of damaged, deformed or corroded structural members, bracing, connection plates and base plates. Inspect the anchor bolts and base-plate connections, particularly at the column bases, and replace damaged or severely corroded bolts, nuts and washers as required. Tighten and align loose connections and restore the structural stability of the tower in accordance with the approved requirements and SWC specifications. 2. Concrete Foundation Repairs Inspect concrete components using hammer test or equivalent methods to asses concrete durability, test is done to grade beams, pedestals, foundations, columns and other structural elements. Works shall include removal of loose concrete, treatment of exposed reinforcement and anchor bolts, crack repair using approved structural repair mortar or epoxy injection as appropriate, and reinstatement of damaged concrete with approved structural repair mortar/micro-concrete. Severely damaged sections shall be repaired or replaced as required 3. Tank Shell and Leakage Repair Inspect the tank internally and externally for all leakage points, corroded areas and damaged joints or panels. Repair leaking joints and welds, tighten or replace defective/corroded bolts, nuts and washers, replace damaged gaskets/sealing materials, and repair or replace severely corroded or perforated steel panels with suitable steel plates. Repair and seal pipe penetrations, flanges and other fittings where required. Carry out a water-tightness test after completion. 4. Internal and External Tank Coating Prepare the internal tank surfaces by removing rust, scale, loose coating and contaminants. Apply an approved anti-corrosion primer followed by two coats of certified potable-water-grade epoxy lining, suitable for contact with drinking water, in accordance with the manufacturer's requirements. Prepare the external tank surfaces and apply two coats of approved anti-corrosion primer and one durable weather-resistant finishing coat, including all necessary touch-up works. 5. Tower Cleaning and Painting Clean and prepare the complete steel tower, including columns, bracing and connections, removing rust, loose paint and contaminants. Apply two coats of approved anti-corrosion primer and one final weather-resistant finishing coat. 6. Valves and Pipework Rehabilitate the existing 3-inch isolation gate valves, including replacement of defective gaskets, bolts, nuts, washers and other accessories, and reconnect them to the existing pipework. Supply and install the required length of 3-inch galvanized steel (GI) pipe, ASTM standard, for the supply and delivery lines, including all required fittings, bends, tees, sockets, flanges, reducers, unions and other accessories. The work shall include modification and sealing of the existing tank shell pipe penetrations as required to accommodate the new pipework and ensure watertight connections. The pipework shall be securely supported using suitable pipe clamps/hangers and brackets at appropriate spacing. The item shall include all necessary cutting, threading, joining, supports, fittings, accessories. 7. Overflow Valve/Manhole and Fittings Repair or replace the existing overflow valve/manhole cover, sockets, flanges, gaskets and stainless-steel bolts as required, including all associated fittings and accessories. 8. Access Ladder Safety Protection Repair the ladder to restore the functionality and fabricate and install a circular safety protection cage around the access ladder using 16 mm diameter steel bars and hoops, commencing approximately 2 m above ground level, including fixing, welding, corrosion protection and painting, in accordance with the approved drawings and safety requirements. 9. Internal Bracing Inspect all internal bracing members for corrosion, deformation, cracks and loose or missing connections. Replace damaged or severely corroded bracing members where required, including corroded or missing bolts, nuts and washers. Reinstate and secure all connections and apply suitable corrosion protection in accordance with SWC specifications. 10. Cleaning, Disinfection and Final Testing Upon completion, thoroughly clean and wash the tank, disinfect it using an approved potable-water disinfection procedure, and carry out final watertightness, leakage and operational tests to confirm that the tank is safe, watertight and fully operational. | Job | 1
D.13 | Construction of Water Distribution Stand Construct a water distribution stand measuring approximately 3.0 m long × 0.8 m high × 0.6 m deep, using good-quality first-class bricks. Apply cement mortar plaster using a 1:6 cement-to-sand mix, with SBR bonding/admixture at 2 litres per 50 kg cement bag, in accordance with the manufacturer's recommendations. 2. Concrete Slab and Drainage Excavate an area of 6.0 m × 3.0 m × 200 mm deep and backfill with 150 mm of approved selected material, compacted mechanically in suitable layers. Construct a 6.0 m × 3.0 m × 150 mm reinforced concrete slab using 1:2:4 concrete mix, reinforced with 12 mm diameter steel bars at 150 mm spacing in both directions. Provide a suitable slope to ensure positive drainage away from the distribution point and connect the slab to the surrounding ground to land scape tress to prevent water ponding. 3. Galvanized Steel Pipework • Supply and install approximately 5 m of 3-inch galvanized steel pipe connected to the distribution stand, including all required fittings and accessories include 3 inch gate valve PN10. • Supply and install approximately 20 m of 3-inch galvanized steel pipe from the tank discharge, including all required fittings and accessories. • Buried pipework shall be installed at approximately 300 mm below ground level, including excavation and backfilling. • Galvanized/metallic pipework shall be cleaned and protected with two coats of approved anti-corrosion paint. 4. Service Outlets and Hoses Provide two service outlets, each complete with: • Connection from the 3-inch main through a 3-inch × 2-inch tee; • Required cutting, threading and connection works; • 2-inch full-bore ball valve with lever handle; • 10 m long, 2-inch flexible hose; • Hose couplings/connectors, nozzles and stainless-steel clamps; • All required fittings and accessories. Provide suitable galvanized wall-mounted hose hangers/brackets to keep the hoses elevated and prevent contact with the ground when not in use. 5. Excavation, Backfilling and Testing The scope shall include all necessary excavation, selected-material filling, mechanical compaction, backfilling, concrete works, pipe supports, fittings, accessories, pressure/leakage testing and commissioning required to provide a complete and operational installation. | Job | 1
D.14 | Supply, transport, and plant five (5) trees at the Distribution Point , including site preparation, setting out, excavation of planting pits measuring 600 mm × 600 mm × 1,000 mm deep, backfilling with approved fertile topsoil mixed with organic fertilizer, planting of healthy nursery-grown trees, initial watering, staking where required, mulching, and all necessary materials, labor, tools, and equipment. The contractor shall maintain the trees during the establishment period, including regular watering and replacement of any trees that fail to survive, to ensure healthy growth and successful establishment. to be assessed during the site visit. | No | 5
E | Signboard
E.1 | Supply, fabrication, transportation, and installation of a project signboard comprising four (4) steel panels, each measuring 150 × 30 cm, mounted on a steel frame fabricated from 60 × 30 mm box section steel, 3 mm thick. The signboard panels shall be manufactured from 1.2 mm thick steel sheets, with a clear 80 mm gap between adjacent panels. The panels shall be fixed to steel support legs fabricated from 3-inch (75 MM) DIAMETER Circular steel pipe, 3 mm thick wall thickness, securely anchored into two (2) pits, each measuring 50 × 50 × 50 cm, using plain concrete (1:3:6 mix). The item shall include surface preparation, application of an anti-rust primer, and three coats of oil-based paint, finished with a white background and blue lettering, in accordance with the approved mock-up drawings and the directions of the IOM Engineer. The rate shall include all materials, accessories, labor, tools, equipment, transportation, and complete installation, fully finished and ready for use. | No | 3
TOTAL COST

## Summary of BOQ
Summary of BOQ
BoQ | Description | Total (USD)
Rehab. of Jabal Moya WTP
Two(2) stances toilet Banat
Rehab. of Jabal Moya Booster Kumur Alnayer
Two(2) stances toilet block Kamar Al-Nayer booster
Rehab. of main transmission line
Rehab of water tanks
Grand Total
Amount in writing ( Only …................................................................................................................................)
Signature:
Name:
Stamp