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SISSIRP – Rehabilitation and Upgrading of Hasahisa Hospital
SCOPE OF WORK (SOW) & TECHNICAL SPECIFICATIONS
Location: Al-Hasahisa Hospital, Al Jazira State, Sudan
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[bookmark: _Toc239061481]SECTION I: SCOPE OF WORK
[bookmark: _Toc239061482]1. Introduction
The Works comprise the comprehensive rehabilitation, upgrading, repair, replacement, construction, installation, testing, commissioning, training, and handover of selected buildings, utility systems, healthcare support infrastructure, and external works within Al-Hasahisa Hospital.
The objective of the Project is to improve the functionality, safety, resilience, environmental health conditions, infection prevention standards, and service delivery capacity of the Hospital through integrated civil, architectural, mechanical, electrical, plumbing, sanitary, HVAC, and external infrastructure interventions.
The Contractor shall provide all labor, supervision, materials, equipment, tools, transportation, fuel, testing equipment, consumables, temporary facilities, storage areas, permits, quality control measures, safety provisions, and all ancillary services necessary for the complete execution and successful completion of the Works.
[bookmark: _Toc239061483]2. General Requirements
[bookmark: _Toc239061484]2.1 Mobilization and Site Establishment
The Contractor shall:
· Mobilize all personnel, machinery, equipment, and construction resources.
· Establish temporary site offices, stores, workshops, sanitary facilities, and staff welfare facilities.
· Provide temporary water and power supplies.
· Install project signboards and informational signage.
· Establish site fencing, barriers, and security controls.
· Provide communications and project management facilities.
· Maintain site security throughout the Contract period.
· Remove all temporary facilities upon completion.
· The Contractor shall engage a qualified Civil Engineer and (other specialties to be added as needed) to supervise and oversee the execution of the relevant works throughout the project implementation.
[bookmark: _Toc239061485]2.2 Verification of Existing Conditions
Prior to commencing any work, the Contractor shall:
· Verify site conditions and dimensions.
· Verify service routes and utility connections.
· Verify levels and setting-out information.
· Inspect all structures scheduled for rehabilitation.
· Confirm compatibility of proposed works with existing installations.
Any discrepancies shall be reported to the Engineer before execution.
[bookmark: _Toc239061486]2.3 Hospital Operations and Infection Prevention
As the Hospital may remain operational during implementation, the Contractor shall:
· Maintain uninterrupted hospital operations to the maximum extent possible.
· Develop and implement phased construction programs.
· Maintain access for patients, staff, ambulances, and service vehicles.
· Provide temporary partitions and dust barriers.
· Control construction noise and vibration.
· Maintain emergency escape routes and emergency access.
· Implement Infection Prevention and Control (IPC) procedures.
· Protect medical equipment and healthcare spaces.
· Prevent contamination of clinical and patient-care areas.
[bookmark: _Toc239061487]2.4 Health, Safety and Environmental Management
The Contractor shall prepare and implement:
· Site-Specific Health and Safety Plan.
· Environmental Management Plan.
· Waste Management Plan.
· Infection Control Management Plan.
· Traffic Management Plan.
· Emergency Response Plan.
· Fire Prevention and Protection Plan.
The Contractor shall provide all required personal protective equipment and shall ensure compliance with applicable national and international safety standards.
[bookmark: _Toc239061488]2.5 Quality Assurance and Submittals
The Contractor shall submit for approval:
· Work Program.
· Method Statements.
· QA/QC Plan.
· Material Approval Requests.
· Shop Drawings.
· Equipment Data Sheets.
· Samples of finishes and fixtures.
No work shall commence without the required approvals.
[bookmark: _Toc239061489]3. Demolition and Removal Works
The Contractor shall undertake all demolition, dismantling, removal, disposal, and preparatory works necessary to facilitate rehabilitation activities including:
· Removal of damaged roofing components.
· Removal of defective waterproofing systems.
· Removal of damaged ceilings.
· Removal of deteriorated floor finishes.
· Removal of damaged wall tiles.
· Removal of defective doors and windows.
· Removal of damaged plaster and render.
· Removal of deteriorated paints and coatings.
· Removal of damaged plumbing fixtures.
· Removal of obsolete piping systems.
· Removal of non-functional electrical installations.
· Removal of damaged HVAC equipment.
· Removal of obsolete drainage components.
· Removal of unsuitable construction materials.
· Removal and disposal of debris from site.
All demolition works shall be executed carefully to avoid damage to adjacent structures and ongoing hospital operations.
[bookmark: _Toc239061490]4. Civil and Structural Rehabilitation Works
The Contractor shall carry out all civil and structural rehabilitation works necessary for the restoration and upgrading of the hospital buildings and associated infrastructure.
[bookmark: _Toc239061491]4.1 Concrete Works
Works shall include:
· Excavation for foundations and structures.
· Blinding concrete.
· Reinforced concrete foundations.
· Reinforced concrete slabs.
· Concrete plinths.
· Concrete bases for equipment.
· Concrete ramps.
· Concrete covers.
· Concrete repair works.
· Concrete manholes.
· Concrete septic tanks.
· Concrete soakaway structures.
· Concrete channels and drainage structures.
[bookmark: _Toc239061492]4.2 Masonry Works
Works shall include:
· Construction of brick masonry walls.
· Block masonry walls.
· Repair of existing masonry.
· Reconstruction of damaged walls.
· Internal partition walls.
· Utility structures.
· Boundary wall rehabilitation.
· Incinerator masonry works.
[bookmark: _Toc239061493]4.3 Structural Repairs
The Contractor shall undertake:
· Repair of cracked walls.
· Structural strengthening works.
· Concrete patch repairs.
· Repair of lintels and openings.
· Repair of verandas and canopies.
· Restoration of structurally deteriorated elements.
[bookmark: _Toc239061494]5. Roofing and Waterproofing Works
[bookmark: _Toc239061495]5.1 Roofing Works
The Contractor shall:
· Remove damaged roof coverings.
· Repair and strengthen roof support structures.
· Supply and install new roofing sheets where required.
· Replace ridges, flashings, caps, and accessories.
· Repair roof drainage components.
· Ensure complete weatherproofing of roofing systems.
[bookmark: _Toc239061496]5.2 Waterproofing Works
Works shall include:
· Roof waterproofing systems.
· Waterproof screeds.
· Acrylic waterproofing applications.
· Waterproof coatings.
· Joint sealing.
· Waterproof treatment of wet areas.
· Flood testing of waterproofed surfaces.
[bookmark: _Toc239061497]5.3 Roof Protection and Insulation
The Contractor shall provide:
· Roof insulation systems where required.
· Moisture barriers.
· Thermal protection treatments.
· Protection against solar exposure and water penetration.
[bookmark: _Toc239061498]6. Ceiling Works
The Works shall include:
· Repair of existing ceilings.
· Replacement of damaged ceilings.
· Installation of suspended gypsum ceilings.
· Ceiling support framework.
· Access panels.
· Ceiling finishing and painting.
· Moisture-resistant ceiling systems in wet areas.
[bookmark: _Toc239061499]7. Architectural Finishes
[bookmark: _Toc239061500]7.1 Plaster Works
Works shall include:
· Internal plastering.
· External plastering.
· Crack treatment.
· Surface preparation.
· Repair of damaged render.
· Cement-sand plaster finishes.
[bookmark: _Toc239061501]7.2 Floor Finishes
The Contractor shall provide:
· Porcelain floor tiling.
· Ceramic floor tiling.
· Epoxy flooring where specified.
· Stair finishes.
· Skirtings.
· Floor preparation and leveling.
[bookmark: _Toc239061502]7.3 Wall Finishes
Works shall include:
· Ceramic wall tiles.
· Hygienic finishes.
· Moisture-resistant finishes.
· Internal wall treatments for healthcare environments.
[bookmark: _Toc239061503]7.4 Painting Works
The Contractor shall carry out:
· Surface preparation.
· Internal painting.
· External painting.
· Ceiling painting.
· Protective coatings.
· Anti-fungal coatings.
· Weather-resistant external coatings.
[bookmark: _Toc239061504]8. Doors, Windows and Metal Works
[bookmark: _Toc239061505]8.1 Doors
The Contractor shall supply and install:
· Steel doors.
· Aluminum doors.
· Security doors.
· Lead-lined doors where required.
· Door hardware and accessories.
· Door frames and architraves.
[bookmark: _Toc239061506]8.2 Windows
Works shall include:
· Aluminum-framed windows.
· Glass glazing.
· Window screens.
· Window accessories.
· Window rehabilitation works.
[bookmark: _Toc239061507]8.3 Metal Works
Works shall include:
· Security grilles.
· Handrails.
· Expanded metal mesh.
· Steel fabrication works.
· Protective guards.
· Access ladders.
· Miscellaneous metal components.
[bookmark: _Toc239061508]9. Water Supply and Plumbing Works
The Contractor shall rehabilitate and upgrade the complete water supply and plumbing systems serving the Hospital.
[bookmark: _Toc239061509]9.1 Water Distribution Network
Works shall include:
· PPR pipe networks.
· Isolation valves.
· Pipe fittings.
· Pipe supports and accessories.
· Connections to existing systems.
· Pressure testing and commissioning.
[bookmark: _Toc239061510]9.2 Water Storage Systems
The Contractor shall provide:
· Potable water storage tanks.
· Tank support structures.
· Pipe connections and accessories.
· Overflow and drainage arrangements.
· Tank disinfection and commissioning.
[bookmark: _Toc239061511]9.3 Booster Pump Systems
Works shall include:
· Booster pumps.
· Pump control panels.
· Valves and accessories.
· Electrical power connections.
· Testing and commissioning.
[bookmark: _Toc239061512]9.4 Plumbing Fixtures
The Contractor shall supply and install:
· Water closets.
· Squat toilets.
· Wash basins.
· Faucets and mixers.
· Floor drains.
· Healthcare-grade sanitary fixtures.
· Plumbing accessories.
[bookmark: _Toc239061513]10. Sanitary Sewerage and Drainage Works
[bookmark: _Toc239061514]10.1 Sewerage Network
Works shall include:
· UPVC drainage pipes.
· Waste and vent systems.
· Building connections.
· Excavation and backfilling.
· Testing and commissioning.
10.2 Manholes and Inspection Chambers
The Contractor shall construct and rehabilitate:
· Inspection chambers.
· Manholes.
· Covers and frames.
· Benching and channels.
[bookmark: _Toc239061515]10.3 Septic Tank System
Works shall include:
· Excavation.
· Reinforced concrete septic tanks.
· Internal partition walls.
· Waterproofing.
· Ventilation systems.
· Covers and access openings.
· Water-tightness testing.
[bookmark: _Toc239061516]10.4 Soakaway Pits
The Contractor shall construct soakaway systems including:
· Excavation.
· Filter media.
· Reinforced concrete or masonry lining.
· Covers.
· Testing and commissioning.
[bookmark: _Toc239061517]10.5 Stormwater Drainage
Works shall include:
· Surface drains.
· Drainage channels.
· Area drainage improvements.
· Site runoff management.
[bookmark: _Toc239061518]11. Electrical Works
The Contractor shall rehabilitate and upgrade the electrical infrastructure throughout the Hospital.
11.1 Power Distribution
Works shall include:
· Main distribution boards.
· Sub-distribution boards.
· Circuit breakers.
· Isolators.
· Cabling.
· Conduits and accessories.
· Earthing and bonding systems.
[bookmark: _Toc239061519]11.2 Lighting Systems
The Contractor shall provide:
· LED lighting fixtures.
· Internal lighting.
· External lighting.
· Clinical lighting.
· Lighting controls and switches.
[bookmark: _Toc239061520]11.3 Small Power Installations
Works shall include:
· Socket outlets.
· Dedicated equipment outlets.
· Air-conditioning power outlets.
· Switching devices.
· Associated wiring.
[bookmark: _Toc239061521]11.4 Testing and Commissioning
The Contractor shall undertake:
· Continuity testing.
· Insulation resistance testing.
· Earth resistance testing.
· Functional testing.
· Final commissioning of all electrical systems.
[bookmark: _Toc239061522]12. HVAC and Ventilation Works
[bookmark: _Toc239061523]12.1 Air Conditioning Systems
The Contractor shall provide:
· Split air-conditioning systems.
· Indoor units.
· Outdoor units.
· Refrigerant pipework.
· Condensate drainage.
· Controls and accessories.
[bookmark: _Toc239061524]12.2 Ventilation Systems
Works shall include:
· Exhaust fans.
· Wall-mounted fans.
· Ceiling fans.
· Mechanical ventilation systems.
[bookmark: _Toc239061525]12.3 Commissioning
The Contractor shall undertake:
· Pressure testing.
· Vacuum testing.
· Refrigerant verification.
· Balancing.
· Functional testing.
[bookmark: _Toc239061526]13. Specialized Healthcare Facility Works
The Contractor shall execute specialized healthcare-related interventions including:
· Radiology and imaging area improvements.
· Radiation protection elements where required.
· Infection-control finishes.
· Clinical support spaces.
· Utility upgrades serving healthcare functions.
[bookmark: _Toc239061527]14. Medical Waste Management Facilities
The Contractor shall construct and commission a medical waste incinerator complete with:
· Site preparation.
· Concrete foundations.
· Combustion chambers.
· Refractory brick lining.
· Chimney installation.
· Loading doors.
· Ash removal systems.
· Protective metal works.
· Operator access arrangements.
· Testing and commissioning.
The completed system shall be suitable for treatment of infectious healthcare waste.
[bookmark: _Toc239061528]15. External Works
[bookmark: _Toc239061529]15.1 Site Infrastructure
Works shall include:
· Site grading.
· Earthworks.
· Restoration of disturbed areas.
· Surface drainage improvements.
[bookmark: _Toc239061530]15.2 Access and Circulation
The Contractor shall provide:
· Access ramps.
· Pedestrian walkways.
· Service access improvements.
· Connections between buildings.
[bookmark: _Toc239061531]15.3 Boundary and Security Works
Works shall include:
· Boundary wall rehabilitation.
· Security improvements.
· Gates.
· Fencing.
· Protective screens.
[bookmark: _Toc239061532]15.4 External Utilities
The Contractor shall execute:
· Water network extensions.
· External drainage works.
· Utility connections.
· Service coordination works.
[bookmark: _Toc239061533]16. Testing, Commissioning and Training
The Contractor shall perform comprehensive testing and commissioning of all building systems and infrastructure including:
· Water supply systems.
· Plumbing systems.
· Sewerage systems.
· Septic tanks and soakaways.
· Electrical systems.
· Lighting systems.
· HVAC systems.
· Medical waste incinerator.
· Architectural and building elements.
The Contractor shall provide operational training to designated Hospital staff and submit all corresponding training records.
[bookmark: _Toc239061534]17. Handover Requirements
The Contractor shall submit:
· As-built drawings.
· Testing and commissioning reports.
· QA/QC records.
· Material certificates.
· Operation and Maintenance Manuals.
· Equipment warranties.
· Manufacturer guarantees.
· Preventive maintenance schedules.
· Spare parts lists.
· Training records.
The Works shall be considered complete only after successful testing and commissioning, correction of all defects, submission of required documentation, final cleaning, and issuance of formal acceptance by the Employer.





[bookmark: _Toc236854390][bookmark: _Toc238043168][bookmark: _Toc238382587][bookmark: _Toc239059970][bookmark: _Toc239061535]SECTION II: PROJECT TECHNICAL SPECIFICATIONS
To Be Read Together with the SISSIRP Unified Technical Specifications.
"To be read in conjunction with the SISSIRP Unified Technical Specifications. In case of discrepancies between the unified specifications and item-specific descriptions, the provisions of this document shall prevail, subject to the approval of the IOM Engineer."
[bookmark: _Toc236854391][bookmark: _Toc238043169][bookmark: _Toc238382588][bookmark: _Toc239059971][bookmark: _Toc239061536]Division 03: Concrete Works 
[bookmark: _Toc236854392][bookmark: _Toc238043170][bookmark: _Toc238382589][bookmark: _Toc239059972][bookmark: _Toc239061537]General
Concrete works shall include all reinforced concrete elements required under the rehabilitation works, including:
· Roof screeds.
· Water tank supports.
· Pump foundations.
· Manholes.
· Septic tank structures.
· Soak-away structures.
· Access slabs.
· Stair repairs.
· Structural rehabilitation works.
[bookmark: _Toc236854393][bookmark: _Toc238043171][bookmark: _Toc238382590][bookmark: _Toc239059973][bookmark: _Toc239061538]Materials
[bookmark: _Toc236854394][bookmark: _Toc238043172]Cement
· Ordinary Portland Cement shall comply with:
· ASTM C150 Type I
· BS EN 197-1
· Sudanese standards where applicable.
Cement older than three months from the date of manufacturing shall not be used.
[bookmark: _Toc236854395][bookmark: _Toc238043173][bookmark: _Toc238382591][bookmark: _Toc239059974][bookmark: _Toc239061539]Aggregates
Aggregates shall comply with ASTM C33.
Maximum aggregate size:
· 20 mm for reinforced concrete.
· 10 mm for repair works and toppings.
[bookmark: _Toc236854396][bookmark: _Toc238043174][bookmark: _Toc238382592][bookmark: _Toc239059975][bookmark: _Toc239061540]Reinforcement
High-yield deformed bars:
· fy = 460 MPa minimum.
Steel shall be free from:
· oil
· mud
· loose rust
· paint
[bookmark: _Toc236854397][bookmark: _Toc238043175][bookmark: _Toc238382593][bookmark: _Toc239059976][bookmark: _Toc239061541]Concrete Strength
	Application
	Minimum Strength

	Blinding
	C15

	Manholes
	C20

	Septic tanks
	C25

	Structural repair works
	C25

	Water tank supports
	C25



[bookmark: _Toc236854398][bookmark: _Toc238043176][bookmark: _Toc238382594][bookmark: _Toc239059977][bookmark: _Toc239061542]Testing
The Contractor shall provide:
· Slump test for every pour.
· Six concrete cubes for every 50 m³.
· 7-day and 28-day compressive strength tests.
· Crushing Reports: All data provided by the independent testing facility must log the failure load in Kilonewtons (kN), the surface area of the test specimen in square millimeters (mm²), and the final calculated strength converted precisely into N/mm².
· Non-Compliance: Any sample batch registering a crushing strength below 30 N/mm² at the 28-day interval will be flagged as a structural failure, prompting immediate halting of subsequent works and mandatory core-testing.
[bookmark: _Toc235707001][bookmark: _Toc236854399][bookmark: _Toc238043177][bookmark: _Toc238382595][bookmark: _Toc239059978][bookmark: _Toc239061543]Execution, Workmanship, and Quality Control
· Mechanical Compaction: Immediately following placement, all fresh concrete must be thoroughly compacted around the steel reinforcement mesh using mechanical needle vibrators to eliminate air pockets, honeycombing, and voids.
· Curing Requirements: Exposed concrete surfaces must be kept continuously damp via continuous water spraying or ponding system to ensure slow hydration and prevent shrinkage cracks until the 30 N/mm² design strength is achieved.
· Engineering Clearance: No concrete pouring shall begin until the supervising engineer checks and signs off on the formwork alignment, rigid bracing, cleanliness, and structural steel reinforcement spacing.
[bookmark: _Toc236843844][bookmark: _Toc236854400][bookmark: _Toc238043178][bookmark: _Toc238382596][bookmark: _Toc239059979][bookmark: _Toc239061544]Hot-Weather Concreting
[bookmark: _Toc236843845][bookmark: _Toc236854401][bookmark: _Toc238043179][bookmark: _Toc238382597][bookmark: _Toc239059980][bookmark: _Toc239061545] General Requirements
· Standard Compliance: All concrete works executed during hot weather conditions shall strictly comply with the technical frameworks of BS EN 206 and BS 8500.
· Applicability: This clause applies to all in-situ concrete works irrespective of individual element volume or mix.
[bookmark: _Toc236843846][bookmark: _Toc236854402][bookmark: _Toc238043180][bookmark: _Toc238382598][bookmark: _Toc239059981][bookmark: _Toc239061546]Temperature Controls & Materials
· Concrete Discharge Temperature: The temperature of fresh concrete at the point of discharge shall not exceed 35°C, unless specialized, engineer-approved cooling measures are implemented.
· Cement Storage and Delivery Temperature: Cement powder at the time of mixing shall not exceed 80°C. Bagged cement must be stored in a shaded, well-ventilated weatherproof structure, elevated off the ground, and protected from direct solar heat gain to prevent flash setting and thermal cracking.
· Pre-cooling Measures: The Contractor shall utilize chilled batch water, flake ice, or shaded aggregate stockpiles to maintain the specified temperature thresholds. 
[bookmark: _Toc236843847][bookmark: _Toc236854403][bookmark: _Toc238043181][bookmark: _Toc238382599][bookmark: _Toc239059982][bookmark: _Toc239061547]Execution & Placement
· Substrate Preparation: Formwork, reinforcement, and subgrades shall be thoroughly pre-wetted with cool water immediately prior to placement to prevent the rapid absorption of mix water.
· Scheduling Restrictions: Concrete placement shall be rescheduled to cooler periods of the day (early morning or night) if ambient temperatures jeopardize setting times or workability.
· Delivery Timeframes: Transit and waiting times for ready-mix concrete delivery trucks shall be minimized to prevent premature slump loss.
[bookmark: _Toc236843848][bookmark: _Toc236854404][bookmark: _Toc238043182][bookmark: _Toc238382600][bookmark: _Toc239059983][bookmark: _Toc239061548] Curing and Protection
· Initial Curing: Curing operations must commence immediately following final finishing preventing plastic shrinkage cracking caused by high evaporation rates.
Method & Duration: Continuous wet curing (moist burlap/ponding) or approved chemical curing membranes shall be maintained for a minimum of 7 consecutive days.
[bookmark: _Toc236854405][bookmark: _Toc238043183][bookmark: _Toc238382601][bookmark: _Toc239059984][bookmark: _Toc239061549]Division 07 –Waterproofing and Roof Protection
[bookmark: _Toc236854406][bookmark: _Toc238043184][bookmark: _Toc238382602][bookmark: _Toc239059985][bookmark: _Toc239061550]2.1 Roof Slope Screed
Roof screed (Khafjah) indicated in the BOQ shall:
· Achieve minimum slope of 1:40;
· Use cement: sand ratio of 1:3;
· have minimum thickness of 40 mm at high points;
· Contain waterproofing admixture approved by the Engineer.
· The surface shall be free from ponding after completion.
· Maximum standing water after rainfall is 5 mm.
[bookmark: _Toc236854407][bookmark: _Toc238043185][bookmark: _Toc238382603][bookmark: _Toc239059986][bookmark: _Toc239061551]2.2 Acrylic Waterproofing System
The acrylic waterproofing system referenced in the BOQ shall be equivalent to:
· Mixguard AC,
· SikaTop Seal 107,
· Ceresit CR166, or
· Approved equivalent.
Properties:
· Crack bridging.
· Flexible.
· UV resistant.
· Suitable for Sudan climate.
Application:
· Minimum two coats.
· Total dry film thickness not less than 2 mm.
[bookmark: _Toc236854408][bookmark: _Toc238043186][bookmark: _Toc238382604][bookmark: _Toc239059987][bookmark: _Toc239061552]2.3 Flood Testing
Completed waterproofed areas shall undergo:
· 72-hour ponding test.
Acceptance Criteria:
· No leakage;
· No dampness;
· No visible deterioration.
[bookmark: _Toc236854409][bookmark: _Toc238043187][bookmark: _Toc238382605][bookmark: _Toc239059988][bookmark: _Toc239061553]Division 08 – Doors, Windows and Metal Works
[bookmark: _Toc236854410][bookmark: _Toc238043188][bookmark: _Toc238382606][bookmark: _Toc239059989][bookmark: _Toc239061554]3.1 Steel Doors
Steel doors shall comprise:
Frame
· RHS 40 × 80 × 2 mm.
· Fully welded.
Door Leaf
· RHS 30 × 60 × 2 mm.
· 1.2 mm minimum steel sheet.
· Internal stiffeners at maximum 400 mm spacing.
[bookmark: _Toc236854411][bookmark: _Toc238043189][bookmark: _Toc238382607][bookmark: _Toc239059990][bookmark: _Toc239061555]3.2 Finishing
All steelwork shall receive:
· One zinc-rich primer coat;
· Two anti-rust coats;
· Two enamel finishing coats.
Dry film thickness:
· Minimum 100 microns.
[bookmark: _Toc236854412][bookmark: _Toc238043190][bookmark: _Toc238382608][bookmark: _Toc239059991][bookmark: _Toc239061556]3.3 Aluminum Windows
Aluminum sections shall:
· Minimum 1.4 mm thickness;
· Powder-coated finish;
· 60–80 micron coating thickness.
Glass:
· Minimum 6 mm clear glazing.
3.4 [bookmark: _Toc235707058][bookmark: _Toc236854413][bookmark: _Toc238043191][bookmark: _Toc238382609][bookmark: _Toc239059992][bookmark: _Toc239061557]Technical Specifications 
3.5 [bookmark: _Toc235707059][bookmark: _Toc236854414][bookmark: _Toc238043192][bookmark: _Toc238382610][bookmark: _Toc239059993][bookmark: _Toc239061558]Pre-Installation Iron Framing
· Material Profile: High-tensile structural steel rectangular hollow sections (RHS) measuring 80mm × 40mm (8cm × 4cm).
· Treatment: Shop-applied anti-corrosive red-oxide primer layer before structural installation into masonry surrounds.
3.6 [bookmark: _Toc235707060][bookmark: _Toc236854415][bookmark: _Toc238043193][bookmark: _Toc238382611][bookmark: _Toc239059994][bookmark: _Toc239061559]Passageways, Operation Rooms, and Bathrooms, Doors & Windows
· Aluminum Extrusions: Genuine Saudi aluminum architectural profiles featuring a 2mm material wall thickness.
· Glazing (Glass Panels): 6mm thick, tempered or high-strength architectural tinted glass, set with premium EPDM rubber gaskets.
· Hardware & Accessories:
· Heavy-duty commercial hydraulic door closers configured with adjustable latching speeds.
· Stainless steel institutional handles, heavy-gauge commercial locksets, and perimeter trim.
· Heavy-duty ball-bearing sliding track assemblies for the operation room doors.
· Size Variations (Doors):
· Standard Passageway/Zone Doors: 2.0m × 2.2m | 2.7m × 2.2m | 1.4m × 2.2m | 1.0m × 2.2m | or as in BOQ.
· Bathroom Doors: 0.80m × 2.2m
· Operation Room Doors (Sliding Type): 1.5m × 2.2m
· Size Variations (Windows):
· Standard Architectural Windows: 1.4m × 1.8m | 3.0m × 2.0m | or as in BOQ
3.7 [bookmark: _Toc235707061][bookmark: _Toc236854416][bookmark: _Toc238043194][bookmark: _Toc238382612][bookmark: _Toc239059995][bookmark: _Toc239061560]Aluminum Skylight Assemblies
· Structural Frame: Built from 2mm thick aluminum profiles matching the performance properties of structural windows.
· Glazing: Weatherproof, high-impact 6mm tinted safety glass featuring UV-resistant commercial perimeter sealants.
· Size Variations (Skylights):
· Staircase Skylights: 0.80m × 1.2m
· Corridor/Zone Skylights: 0.40m × 2.0m
· Bathroom Skylights: 0.60m × 0.60m

3.8 [bookmark: _Toc235707062][bookmark: _Toc236854417][bookmark: _Toc238043195][bookmark: _Toc238382613][bookmark: _Toc239059996][bookmark: _Toc239061561]Ward Partitions
· Profile System: Aluminum structural sections featuring a heavy 4mm profile wall thickness.
· Assembly Elements: Supplied complete with institutional floor/wall fixing bolts, internal privacy panels/glazing, structural connectors, and heavy-duty handles.
3.9 [bookmark: _Toc235707063][bookmark: _Toc236854418][bookmark: _Toc238043196][bookmark: _Toc238382614][bookmark: _Toc239059997][bookmark: _Toc239061562] Execution, Workmanship, and Quality Control
· On-Site Dimensions: The contractor must verify all structural opening sizes on-site prior to completing factory assembly of the aluminum frames. No spacing gaps greater than 5 mm between the steel sub-frame and aluminum frame are permitted.
· Glazing Standards: All 6 mm tinted glass panels must be set inside the aluminum channels using continuous, high-grade EPDM rubber gaskets. Silicone sealants must be applied cleanly along the external perimeter to ensure absolute wind and water tightness.
· Plumb and Level Tolerances: Erect all frames perfectly vertical and level. The maximum allowable installation deviation is 1 mm per meter of height. Diagonal measurements of completed frames must be identical to guarantee perfect squareness.
· Hardware Adjustment: Adjust all automatic door closers and sliding tracks so that doors operate smoothly without requiring excessive force, and latch securely without rattling.
· Protection and Cleaning: Keep all protective factory plastic wrap on the aluminum profiles until final handover. Clean away all structural mortar, plaster splashes, or silicone streaks from the glass and metal surfaces using non-abrasive, non-acidic cleaning agents.

3.10 [bookmark: _Toc235699237][bookmark: _Toc235707067][bookmark: _Toc236854419][bookmark: _Toc238043197][bookmark: _Toc238382615][bookmark: _Toc239059998][bookmark: _Toc239061563] Technical Specifications (Metal Works)
3.10.1 [bookmark: _Toc235707068][bookmark: _Toc236854420][bookmark: _Toc238043198][bookmark: _Toc238382616]Security Grilles (Windows, Skylights, and Secondary Exterior Doors)
· External Perimeter Frame: Heavy-duty, structural steel rectangular hollow section (RHS) pipes measuring 80mm × 40mm (minimum wall thickness 2.0mm).
· Internal Vertical Elements: Structural steel RHS pipes measuring 60mm × 30mm, arrayed vertically with a maximum clear spacing of 200mm center-to-center.
· Internal Horizontal Elements: Structural steel RHS pipes measuring 80mm × 40mm, positioned horizontally every 700mm to form a rigid geometric pentagonal pattern.
· Fastening Hardware: Heavy-duty tamper-proof masonry expansion bolts or chemically anchored steel pins driven at least 80mm deep into concrete structural surrounds.

3.11 [bookmark: _Toc235707069][bookmark: _Toc236854421][bookmark: _Toc238043199][bookmark: _Toc238382617]Staircase Handrails
· Material Composition: Industrial-grade stainless steel (Grade 304 or higher) or heavy-gauge galvanized structural steel pipe profiles.
· Dimensions: Ergonomic top rail diameter between 38mm and 50mm, positioned at a finished height of 900mm to 1000mm measured vertically from the stair tread nosing.
· Structural Supports: Fixed stanchions/posts spaced at a maximum interval of 1200mm, firmly anchored directly into the structural concrete staircase base plates or side walls.

3.12 [bookmark: _Toc235707070][bookmark: _Toc236854422][bookmark: _Toc238043200][bookmark: _Toc238382618]Corrugated Iron Doors (Rooftop & Main Entrance doors)
· Rooftop Staircase Door (1.0m × 2.2m):
· Skin: Heavy-gauge, weather-resistant galvanized corrugated iron sheeting (minimum 1.2mm thickness) welded to a rigid internal square structural steel chassis.
· Hardware: Weatherproof, heavy-duty commercial mortise locksets, stainless steel pull handles, and a minimum of three heavy-duty bullet hinges.
· Main Entrance Door (3.0m × 2.2m):
· Configuration: Double-leaf structural iron gate matching the 2.2-meter clearance, constructed from high-tensile corrugated iron sheets integrated with structural internal bracing.
· Hardware: Heavy-duty industrial slide bolts (top and bottom drop-bolts), high-security institutional padlock eyes, commercial pull bars, and structural-grade pivoting hinges.

3.12.1 [bookmark: _Toc235707071][bookmark: _Toc236854423][bookmark: _Toc238043201][bookmark: _Toc238382619]Paint & Protective Finishes
· Primer Base: Minimum of two (2) separate coats of high-performance zinc-chromate or red-oxide anti-corrosive structural metal primer.
· Finish Coat: Minimum of two (2) coats of premium poly-urethane or industrial-grade gloss enamel paint designed for heavy UV exposure and frequent chemical washing.
3.13 [bookmark: _Toc235699241][bookmark: _Toc235707072][bookmark: _Toc236854424][bookmark: _Toc238043202][bookmark: _Toc238382620][bookmark: _Toc239059999][bookmark: _Toc239061564] Execution & Finishing Workmanship
· Welding: All structural joints must be fully, continuously welded (no spot welding allowed). All welds must be ground smooth, flush, and free of slag or pinholes before painting.
· Plumb & Square Alignment: Install all doors, security frames, and handrails perfectly true, level, and vertically plumb, holding tolerances within a strict ±2mm variance.
· Ergonomic Safety: Ensure all staircase handrail terminations are cleanly returned smooth into the structural wall surface or dropped down to the floor to prevent clothing snags.
· Anti-Corrosion Priming: All steel surfaces must be thoroughly de-rusted, degreased, and treated with at least two coats of zinc-phosphate anti-corrosive primer before leaving the fabrication workshop.
· Tolerances: Frames must be installed strictly plumb and square. Maximum allowable deviation across structural heights is ±2 mm.
· Supervising Engineer Approval: Present the final installed grilles, handrails, and entrance assemblies for close joint inspection and official written sign-off.
[bookmark: _Toc236854425][bookmark: _Toc238043203][bookmark: _Toc238382621][bookmark: _Toc239060000][bookmark: _Toc239061565]4. Plastering Technical Specifications 
4.1 [bookmark: _Toc235707017][bookmark: _Toc236854426][bookmark: _Toc238043204][bookmark: _Toc238382622][bookmark: _Toc239060001][bookmark: _Toc239061566]Material Requirements
· Cement: Premium-quality Ordinary Portland Cement (OPC) free from lumps, moisture, or premature setting.
· Sand: Clean, sharp, well-graded fine river sand, screened to remove clay, loam, shells, organic particles, or chemical impurities.
· Expanded Metal Mesh (Expanda): High-tensile, corrosion-resistant galvanized expanded steel mesh sheet with a minimum width of 30 cm to 40 cm.
· Water: Fresh, potable, clean, and completely free from harmful oils, acids, alkalis, or organic matter.



4.2 [bookmark: _Toc235707018][bookmark: _Toc236854427][bookmark: _Toc238043205][bookmark: _Toc238382623][bookmark: _Toc239060002][bookmark: _Toc239061567]Exterior Plastering (2 cm Thick)
· Application Areas: Exterior walls, inner and outer faces of the roof parapets, and all faces of the stairwell structure.
· Mix Ratio: Strictly 1:6 by volume (1 part cement to 6 parts screened sand).
· Thickness: Applied to a uniform, flat, and plumb total thickness of 2 cm.
· Finish Style: Perfectly smooth, level surface achieved via timber floats and steel trowels. No trowel marks, waves, or surface ripples are permitted.
· Tight Area Integration: Plaster neatly flush up to external electrical junction boxes, switches, and utility fixtures. Maintain sharp, square, orthogonal corners without any messy over-spill.
4.3 [bookmark: _Toc235707019][bookmark: _Toc236854428][bookmark: _Toc238043206][bookmark: _Toc238382624][bookmark: _Toc239060003][bookmark: _Toc239061568]Structural Crack Remediation Method
· Plaster Removal: Chip away and entirely remove the failing, cracked plaster down to the bare red brick masonry substrate. The removal strip must expose at least 15 cm to 20 cm (150–200 mm) of clean masonry on both left and right sides of the crack line.
· Surface Cleaning: Brush away loose dust, mortar fragments, and debris from the exposed masonry channel, then moisten the surface thoroughly.
· Mesh Installation: Position and securely fasten the expanded metal mesh (Expanda) centrally over the crack using galvanized masonry nails or pins. The mesh must extend a minimum of 150 mm to 200 mm past the crack boundary on both sides to distribute tensile stresses.
· Replastering: Apply a primary bonding coat, followed by the finishing plaster coat, ensuring the new surface matches the plane, texture, and level of the surrounding existing plaster perfectly.
4.4 [bookmark: _Toc235707020][bookmark: _Toc236854429][bookmark: _Toc238043207][bookmark: _Toc238382625][bookmark: _Toc239060004][bookmark: _Toc239061569]Execution, Workmanship, and Quality Control
· Scaffolding Safety: Erect independent, rigid external tubular scaffolding fitted with secure working platforms, toe boards, and catch nets along the building perimeter.
· Engineering Sign-off: Do not apply mesh or plaster over cracked zones until the supervising engineer inspects the cleaned masonry substrate and approves the structural preparation.
· Water Curing: Keep all newly applied exterior plaster and repaired crack patches continuously damp by spraying with water at least twice daily for a minimum period of 7 days post-construction to ensure proper hydration and prevent shrinkage cracks.
· Weather Restrictions: Do not apply cement plaster during heavy rain, high winds, or ambient temperatures exceeding 40°C to avoid premature drying or wash-outs.
[bookmark: _Toc236854430][bookmark: _Toc238043208][bookmark: _Toc238382626][bookmark: _Toc239060005][bookmark: _Toc239061570]Division 09 – Finishes
5.1 [bookmark: _Toc236854431][bookmark: _Toc238043209][bookmark: _Toc238382627][bookmark: _Toc239060006][bookmark: _Toc239061571]Ceramic Wall Tiles
Applicable to:
· toilets;
· bathrooms;
· wash areas;
· sanitary rooms.
Requirements:
· Water absorption ≤ 3%.
· Minimum thickness 8 mm.
Installation:
· Cement adhesive C2 grade.
· Joint width 2–3 mm.
5.2 [bookmark: _Toc236854432][bookmark: _Toc238043210][bookmark: _Toc238382628][bookmark: _Toc239060007][bookmark: _Toc239061572]Porcelain Floor Tiles
Porcelain tiles shall be:
· Fully vitrified;
· Water absorption <0.5%;
· Minimum thickness 10 mm.
Slip resistance:
· R10 minimum.
Wet areas:
· R11 minimum.
5.3 [bookmark: _Toc236854433][bookmark: _Toc238043211][bookmark: _Toc238382629][bookmark: _Toc239060008][bookmark: _Toc239061573]Tile Testing
Lippage:
· maximum 1 mm.
Hollow sounding areas:
· maximum 5% of room area.
Defective tiles shall be replaced.
5.4 [bookmark: _Toc235707041][bookmark: _Toc236854434][bookmark: _Toc238043212][bookmark: _Toc238382630][bookmark: _Toc239060009][bookmark: _Toc239061574]Technical Specifications (Tiling Works)
5.4.1 [bookmark: _Toc235707042][bookmark: _Toc236854435][bookmark: _Toc238043213][bookmark: _Toc238382631][bookmark: _Toc239060010][bookmark: _Toc239061575]General Workmanship and Material Cutting
· Edge Precision: All tile cutting must be done using professional wet-saw mechanical cutters to ensure perfectly straight, crisp, unchipped edges. Hand-snapping or jagged manual cuts are strictly prohibited.
· Grouting & Expansion: All joints must be fully packed with a uniform slurry of premium white cement or an approved color-matched grout. Any excess grout must be wiped clean with a damp sponge before it sets.
· Layout Symmetry: Tile layouts must be planned from the center of each room or corridor to ensure balanced, equal-sized cut tiles along the perimeter boundaries.
5.4.2 [bookmark: _Toc235707043][bookmark: _Toc236854436][bookmark: _Toc238043214][bookmark: _Toc238382632][bookmark: _Toc239060011][bookmark: _Toc239061576]Porcelain Tiling (Rooms and Corridors)
· Flooring: Supply and install premium-grade 60 × 60 cm porcelain tiles. Tiles must be bedded on a true-to-level layer of 1:4 cement mortar (1 part cement to 4 parts dry sand). Surfaces must be checked continuously with a spirit level to ensure a completely flat finish with zero lippage.
· Skirting: Supply and install matching porcelain skirting boards cut to a uniform height of 10 cm along all room and corridor perimeters. Skirting must be installed perfectly flush or with a uniform protrusion as approved by the engineer, with top edges smoothly grouted.
5.4.3 [bookmark: _Toc235707044][bookmark: _Toc236854437][bookmark: _Toc238043215][bookmark: _Toc238382633][bookmark: _Toc239060012][bookmark: _Toc239061577]Bathroom Ceramic Tiling
· Bathroom Floors: Supply and install high-quality Egyptian ceramic tiles measuring 30 × 30 cm. These must be bedded on a 1:4 cement mortar mix. The installer must maintain a strict, uniform slope falling toward the floor drainage traps to guarantee that no water ponds on the floor.
· Bathroom Walls: Supply and install matching Egyptian ceramic wall tiles measuring 50 × 30 cm. Tiles must be fixed perfectly plumb using a thin-set mortar or approved tile adhesive over a rough plaster scratch coat, maintaining perfectly aligned horizontal and vertical grout lines.
5.4.4 [bookmark: _Toc235707045][bookmark: _Toc236854438][bookmark: _Toc238043216][bookmark: _Toc238382634][bookmark: _Toc239060013][bookmark: _Toc239061578]Natural Marble Works (Staircases and Entrances)
· Internal Staircase Steps: Supply, cut, and install premium natural marble slabs for the internal staircase steps. The steps must feature a clear width of 1.0 meter, incorporating both the horizontal treads and vertical risers. Slabs must be selected for uniform color, pattern, and grain continuity.
· Internal Staircase Landings: Supply and install matching natural marble slabs for the internal staircase landing zones, ensuring the bedding is perfectly level and flush with the incoming step flights.
· Entrance Staircase Landing: Supply and install heavy-duty natural marble slabs for the main outdoor entrance staircase landing, ensuring a microscopic outward slope to prevent exterior rain puddle formation.
· Entrance Wall Cladding: Supply and install premium natural marble cladding slabs across the walls of the main entrance lobby. Marble panels must be secured using a combination of structural bedding mortar and mechanical stainless-steel anchors or clips to ensure permanent vertical stability.
5.4.5 [bookmark: _Toc235707046][bookmark: _Toc236854439][bookmark: _Toc238043217][bookmark: _Toc238382635][bookmark: _Toc239060014][bookmark: _Toc239061579]External Courtyard Tiling
· Courtyard Floors: Supply and install durable, weather-resistant Egyptian ceramic tiles measuring 40 × 40 cm. Tiles must be bedded on a 1:4 cement mortar layer over a well-compacted sub-base or external concrete apron.
· Slope and Drainage: All courtyard tiling must be precisely sloped toward external storm-water drainage channels or gully traps to ensure efficient surface water runoff during heavy rainfall.
5.5 [bookmark: _Toc235707047][bookmark: _Toc236854440][bookmark: _Toc238043218][bookmark: _Toc238382636][bookmark: _Toc239060015][bookmark: _Toc239061580]Execution, Workmanship, and Quality Control
· Substrate Preparation: Before applying mortar, all concrete floors must be thoroughly swept clean of dust, oil, paint drops, or loose plaster. The bare concrete must be lightly wetted with clean water to prevent it from rapidly absorbing the mixing water from the fresh mortar bed.
· Leveling and Alignment Checks: The contractor must use laser levels or nylon line grids across all rooms and corridors. The supervising engineer will inspect the dry tile layout and leveling lines before permanent mortar setting begins.
· Protection of Finished Works: Newly tiled floors must be barred from all foot traffic for a minimum of 24 hours post-installation. Completed flooring must be covered with protective heavy-duty canvas, building paper, or plastic sheets to prevent scratching or chipping during subsequent construction activities.
· Final Cleansing: Upon completion of all grouting and curing phases, all tiled surfaces must be thoroughly washed with clean water and mild, non-acidic detergents to remove film, dust, and stubborn mortar stains, leaving a flawless, ready-for-handover finish.
[bookmark: _Toc236854441][bookmark: _Toc238043219][bookmark: _Toc238382637][bookmark: _Toc239060016][bookmark: _Toc239061581]Painting
Internal Paint
Acrylic emulsion.
Properties:
· washable;
· anti-fungal;
· low VOC.
Minimum:
· one primer coat;
· two finishing coats.

External Paint
Weather-shield acrylic system:
· UV resistant;
· water resistant;
· anti-carbonation.
Minimum:
· one sealer coat;
· two finish coats.
1.1 [bookmark: _Toc235707024][bookmark: _Toc236854442][bookmark: _Toc238043220][bookmark: _Toc238382638][bookmark: _Toc239060017][bookmark: _Toc239061582]Technical Specifications (Painting)
[bookmark: _Toc235707025][bookmark: _Toc236854443][bookmark: _Toc238043221][bookmark: _Toc238382639][bookmark: _Toc239060018][bookmark: _Toc239061583]6.1.1 Material Standards and Approvals
· Paint Quality: All finishing paints must be first-grade silk paint manufactured by Jotun (e.g., Fenomastic series for interiors, Jota shield series for exteriors) or an approved equivalent premium brand. 
· Sample Submission: Before any paint or putty is delivered to the job site, the contractor must apply mock-up samples (minimum 1.0 m × 1.0 m patches) on the walls for color, texture, and gloss approval by the supervising engineer.
[bookmark: _Toc235707026][bookmark: _Toc236854444][bookmark: _Toc238043222][bookmark: _Toc238382640][bookmark: _Toc239060019][bookmark: _Toc239061584]6.1.2 Interior Walls Painting
· Surface Preparation: Scrap away all loose mortar, dust, and debris. Apply approved high-quality wall putty filler in successive layers. Sand down each layer with fine-grade sandpaper to achieve a perfectly flat, uniform, and plumb surface. 
· Application System: Apply one base primer coat followed by three (3) separate coats of premium plastic emulsion silk paint. Each coat must be allowed to dry completely and be lightly sanded before the next coat is applied. The final surface must be free of brush marks, roller stipples, runs, or color variations. 
[bookmark: _Toc235707027][bookmark: _Toc236854445][bookmark: _Toc238043223][bookmark: _Toc238382641][bookmark: _Toc239060020][bookmark: _Toc239061585]6.1.3 Exterior Walls, Stairwells, and Parapet Walls Painting
· Surface Preparation: Level all rough concrete and masonry substrates using a structural sand-cement mortar rendering coat. Fill all minor voids, blowholes, and surface honeycombing to ensure a uniform plane. 
· Application System: Apply a specialized exterior alkali-resistant primer coat, followed by three (3) separate coats of premium weatherproof exterior silk paint. The final finish must provide robust UV protection and resistance to environmental weathering. 
[bookmark: _Toc235707028][bookmark: _Toc236854446][bookmark: _Toc238043224][bookmark: _Toc238382642][bookmark: _Toc239060021][bookmark: _Toc239061586]6.1.4  Room and Corridor Ceilings Painting
· Surface Preparation: Clean all ceiling concrete surfaces, remove formwork release oils, and apply a thin layer of specialized ceiling putty or joint compound to eliminate imperfections. Sand smoothly. 
· Application System: Apply one primer coat followed by three (3) separate coats of premium plastic emulsion paint, matching the exact surface execution and seamless finish required for the interior walls.

[bookmark: _Toc235707029][bookmark: _Toc236854447][bookmark: _Toc238043225][bookmark: _Toc238382643][bookmark: _Toc239060022][bookmark: _Toc239061587]6.1.5 Execution, Workmanship, and Quality Control
· Protection of Fixtures: Prior to starting any preparation or painting, the contractor must completely mask and protect all floors, electrical boxes, windows, door frames, and completed plaster works using plastic sheeting and masking tape.
· Drying Time Intermissions: The contractor must strictly adhere to the manufacturer’s data sheets regarding drying times between successive coats. No subsequent coat shall be applied until the supervising engineer inspects and approves the previous layer.
· Environmental Constraints: Do not apply exterior paint during dusty conditions, high winds, rain, or when ambient temperatures exceed the maximum limits specified by Jotun (typically 40°C).
· Final Lighting Inspection: The final finished paintwork will be inspected under cross-lighting conditions. Any visible patches, waves, transparency issues, or uneven gloss must be corrected by the contractor at their own expense.

[bookmark: _Toc235707033][bookmark: _Toc236854448][bookmark: _Toc238043226][bookmark: _Toc238382644][bookmark: _Toc239060023][bookmark: _Toc239061588][bookmark: _Toc235707034][bookmark: _Toc236854449]Technical Specifications (Epoxy)Material Requirements
· Epoxy Paint System: Must be a high-build, self-leveling, fiber-reinforced epoxy coating system (such as Epoxy Fiber or an approved medical-grade equivalent) designed for heavy foot traffic, chemical resistance, and sterile environments. 
· [bookmark: _Toc235707035][bookmark: _Toc236854450]Performance Attributes: The cured system must be completely seamless, non-porous, antibacterial, easy to sanitize, and resistant to medical disinfectants, blood, and laboratory chemicals. It must achieve a minimum compressive strength of 50 N/mm² to withstand medical equipment loads. 
7.1  Substrate and Surface Preparation
· Mechanical Profiling: The underlying concrete slab must be thoroughly clean, structurally sound, and completely dry (moisture content must not exceed 4% when tested with a calcium chloride or digital moisture meter). 
· Remediation: Use mechanical floor grinders equipped with dust-extraction vacuums to remove all curing compounds, laitance, old paint, oils, and grease. Blowholes, cracks, and surface pits must be filled flush using an approved solvent-free epoxy putty repair compound. 
· Priming: Apply one uniform coat of a high-penetration epoxy primer to seal the concrete pores and ensure maximum chemical bonding between the substrate and the subsequent epoxy coats.
7.2 [bookmark: _Toc235707036][bookmark: _Toc236854451][bookmark: _Toc238043227][bookmark: _Toc238382645][bookmark: _Toc239060024][bookmark: _Toc239061589]Epoxy Application and Execution
· First Coat Application: Once the primer has cured to a tack-free state, mix the fiber-reinforced epoxy components strictly according to the manufacturer’s instructions using a low-speed mechanical mixer. Apply the first coat uniformly using a notched squeegee or lint-free roller in a single direction (e.g., East-West).
· Second Coat Application: Allow the first coat to dry within the manufacturer's specified recoat window. Apply the second coat exactly perpendicular to the first coat (e.g., North-South). This cross-directional roll ensures a perfectly level surface, uniform thickness, and eliminates any potential pinholes or tracking marks.
· Final Finish: The completed floor system must cure to a perfectly smooth, level, satin or gloss finish with a total dry film thickness (DFT) that complies with the manufacturer's heavy-duty medical traffic data sheets. 
7.3 [bookmark: _Toc235707037][bookmark: _Toc236854452][bookmark: _Toc238043228][bookmark: _Toc238382646][bookmark: _Toc239060025][bookmark: _Toc239061590]  Execution, Workmanship, and Quality Control
· Dust and Contamination Control: Because these are medical delivery, nursery, and laboratory spaces, the application area must be completely sealed off using plastic sheeting isolation barriers. No dust, insects, or floating airborne particles are permitted in the rooms during the application and curing phases.
· Cove Base Integration (Sanitary Detailing): At the junctions where the floor meets the walls, the epoxy must be turned up the wall to create a seamless, radiused cove skirting (typically 10 cm to 15 cm high) if required by the clinical design, eliminating sharp 90-degree corners where bacteria can accumulate.
· Curing Timeline: The treated rooms must be kept under strict climate control (ideally between 15°C and 30°C) and completely locked down. Light foot traffic is restricted for at least 24 hours, and heavy mechanical equipment or medical furniture installation must not occur until a full 7-day chemical cure is reached.
· Testing and Inspection: The supervising engineer will inspect the final cured floor for levelness, complete opacity, the total absence of air bubbles, blisters, or roller lint, and absolute adhesion to the substrate before handover.
[bookmark: _Toc236854453][bookmark: _Toc238043229][bookmark: _Toc238382647][bookmark: _Toc239060026][bookmark: _Toc239061591]Division 22 – Water Supply and Plumbing
7.4 [bookmark: _Toc236854454][bookmark: _Toc238043230][bookmark: _Toc238382648][bookmark: _Toc239060027][bookmark: _Toc239061592]PPR Water Piping
The BOQ requires German-manufactured PPR pipe systems.
Acceptable standards:
· DIN 8077
· DIN 8078
Pressure Class:
	Service
	Rating

	Cold Water
	PN16

	Hot Water
	PN20



7.5 [bookmark: _Toc236854455][bookmark: _Toc238043231][bookmark: _Toc238382649][bookmark: _Toc239060028][bookmark: _Toc239061593] Pipe Installation
Joining method:
· thermal fusion only.
Threaded connections shall not be used except at equipment interfaces.
Pipe supports:
	Pipe Diameter
	Maximum Spacing

	20-25 mm
	1.0 m

	32-50 mm
	1.5 m

	63 mm+
	2.0 m



7.6 [bookmark: _Toc236854456][bookmark: _Toc238043232][bookmark: _Toc238382650][bookmark: _Toc239060029][bookmark: _Toc239061594] Pressure Testing
Hydrostatic test pressure:
· 1.5 times working pressure.
Test duration:
· 2 hours minimum.
Acceptance:
· zero visible leakage;
· pressure loss less than 5%.
7.7 [bookmark: _Toc236854457][bookmark: _Toc238043233][bookmark: _Toc238382651][bookmark: _Toc239060030][bookmark: _Toc239061595] Division 22.4 UPVC Drainage System
Drainage pipes shall be:
· UPVC Schedule 80;
· solvent welded.
Minimum diameters:
	Service
	Diameter

	Basin
	50 mm

	Floor drain
	75 mm

	WC branch
	110 mm

	Main sewer
	160 mm


7.8 [bookmark: _Toc236854458][bookmark: _Toc238043234][bookmark: _Toc238382652][bookmark: _Toc239060031][bookmark: _Toc239061596] Sanitary Fixtures
Western WC
· Vitreous china.
· Dual flush.
· Maximum flush 4.5 liters.
7.9 [bookmark: _Toc236854459][bookmark: _Toc238043235][bookmark: _Toc238382653][bookmark: _Toc239060032][bookmark: _Toc239061597] Squat WC
· Vitreous china.
· Heavy-duty hospital grade.
· Slip-resistant footrests.
7.10 [bookmark: _Toc236854460][bookmark: _Toc238043236][bookmark: _Toc238382654][bookmark: _Toc239060033][bookmark: _Toc239061598] Wash Basins
· Vitreous china.
· Wall mounted.
· Chrome plated mixer.
Working pressure:
· 1-6 bar.
7.11 [bookmark: _Toc236854461][bookmark: _Toc238043237][bookmark: _Toc238382655][bookmark: _Toc239060034][bookmark: _Toc239061599] Division 22.6 Water Storage Tanks
The BOQ includes 2000-liter storage tanks with booster systems.
Tank requirements:
· UV stabilized polyethylene.
· Triple-layer construction.
· Food-grade material.
The tank shall be mounted on:
· galvanized steel support frame.
Design load:
· full water load + 25% safety factor.
7.12 [bookmark: _Toc236854462][bookmark: _Toc238043238][bookmark: _Toc238382656][bookmark: _Toc239060035][bookmark: _Toc239061600] Division 22.7 Booster Pumps
Pump body:
· stainless steel AISI 304.
Impellers:
· stainless steel.
Motor:
· IP55 minimum.
Control panel shall include:
· dry run protection;
· overload protection;
· automatic operation.
7.13 [bookmark: _Toc236854463][bookmark: _Toc238043239][bookmark: _Toc238382657][bookmark: _Toc239060036][bookmark: _Toc239061601]Division 22.8 Septic Tank Construction
The septic tank identified in the BOQ shall be constructed using reinforced concrete.
Internal walls:
· minimum 200 mm thick.
Concrete:
· C25 minimum.
Waterproofing:
· internal cementitious waterproof coating.
7.14 [bookmark: _Toc236854464][bookmark: _Toc238043240][bookmark: _Toc238382658][bookmark: _Toc239060037][bookmark: _Toc239061602]Testing
Before acceptance:
· fill with water;
· retain water for 72 hours.
Permitted leakage:
· none.
7.15 [bookmark: _Toc236854465][bookmark: _Toc238043241][bookmark: _Toc238382659][bookmark: _Toc239060038][bookmark: _Toc239061603]Division 22.9 Soak-Away Pit
The soak-away pit shall:
· be 2 m diameter;
· reach approved depth;
· be lined with masonry or reinforced concrete rings as approved by Engineer.
Surrounding filter media:
· graded crushed stone 25-75 mm.
[bookmark: _Toc236854466][bookmark: _Toc238043242][bookmark: _Toc238382660][bookmark: _Toc239060039][bookmark: _Toc239061604]Division 23 – HVAC
7.15.1 [bookmark: _Toc236854467][bookmark: _Toc238043243][bookmark: _Toc238382661][bookmark: _Toc239060040][bookmark: _Toc239061605]Split Air Conditioning Units
Units shall:
· be inverter type;
· operate at ambient temperatures up to 52°C;
· use R32 refrigerant or approved equivalent.
Minimum EER:
· 3.2
7.15.2 [bookmark: _Toc236854468][bookmark: _Toc238043244][bookmark: _Toc238382662][bookmark: _Toc239060041][bookmark: _Toc239061606]Copper Pipework
Copper tubing:
· ASTM B280.
Insulation:
· closed-cell elastomeric insulation;
· minimum thickness 13 mm.
7.16 [bookmark: _Toc236854469][bookmark: _Toc238043245][bookmark: _Toc238382663][bookmark: _Toc239060042][bookmark: _Toc239061607]Commissioning
Contractor shall perform:
· nitrogen pressure test;
· vacuum test;
· refrigerant charge verification;
· 4-hour operational test.

[bookmark: _Toc236854470][bookmark: _Toc238043246][bookmark: _Toc238382664][bookmark: _Toc239060043][bookmark: _Toc239061608]Division  Electrical Works
7.16.1 [bookmark: _Toc236854471][bookmark: _Toc238043247][bookmark: _Toc238382665][bookmark: _Toc239060044][bookmark: _Toc239061609] Wiring
Conductors:
· stranded copper;
· PVC/XLPE insulated;
· 600/1000 V rated.
Minimum cable sizes:
	Circuit
	Minimum Size

	Lighting
	2.5 mm²

	Socket outlets
	4 mm²

	AC circuits
	6 mm²



7.16.2 [bookmark: _Toc236854472][bookmark: _Toc238043248][bookmark: _Toc238382666][bookmark: _Toc239060045][bookmark: _Toc239061610]Distribution Boards
Distribution boards shall:
· be powder-coated steel;
· IP54 minimum;
· include lockable doors;
· include circuit schedules.
7.16.3 [bookmark: _Toc236854473][bookmark: _Toc238043249][bookmark: _Toc238382667][bookmark: _Toc239060046][bookmark: _Toc239061611]Earthing
Earth roads:
· copper-bonded steel;
· length 3 m minimum.
Maximum earth resistance:
· 5 Ohms.
7.16.4 [bookmark: _Toc236854474][bookmark: _Toc238043250][bookmark: _Toc238382668][bookmark: _Toc239060047][bookmark: _Toc239061612]Testing
The Contractor shall submit certified test reports for:
· Continuity testing.
· Insulation resistance testing.
· Earth resistance testing.
· RCD testing.
· Functional testing.
7.17 [bookmark: _Toc235707051][bookmark: _Toc236854475][bookmark: _Toc238043251][bookmark: _Toc238382669][bookmark: _Toc239060048][bookmark: _Toc239061613]Technical Specifications (Electrical Works)
7.18 [bookmark: _Toc235707052][bookmark: _Toc236854476][bookmark: _Toc238043252][bookmark: _Toc238382670][bookmark: _Toc239060049][bookmark: _Toc239061614]Distribution Equipment and Switches
· Main Distribution Board (MDB): Supply and install a 24-way metal-clad distribution board. The board must feature factory-fitted copper busbars, neutral bars, and isolated earth bars. It must be equipped with a matching 100 Amp safety switch (main circuit breaker) providing over-current and short-circuit protection.
· Power Sockets: Supply and install premium-grade Tenby brand flush-mounted accessories. This includes 13 Amp switched shuttered socket outlets for general ring/radial power circuits and 16 Amp socket outlets for dedicated heavy-appliance radial circuits. 
· A/C Isolators: Supply and install Tenby 45 Amp double-pole (DP) water heater style switches fitted with neon indicators to serve as local isolation switches for all air conditioning units.
7.19 [bookmark: _Toc235707053][bookmark: _Toc236854477][bookmark: _Toc238043253][bookmark: _Toc238382671][bookmark: _Toc239060050][bookmark: _Toc239061615]Lighting and Ventilation Systems
· Room and Hallway Lighting: Supply and install 4-foot Philips fluorescent/Neon light fixtures, complete with electronic ballasts, starter mechanisms, high-efficiency tubes, localized switches, and intermediate wiring connections.
· Bathroom Lighting: Supply and install 2-foot English-made fluorescent/Neon ceiling light fixtures. These units must feature vapor-proof or moisture-resistant enclosures suitable for damp bathroom environments.
· Operating Room Lighting: Supply and install high-intensity, specialized flood lights designed specifically for medical operating rooms. These fixtures must provide shadowless, high-color-rendering illumination, and be safely wired to dedicated clean-power circuits.
· Ceiling Fans: Supply and install heavy-duty 56-inch ceiling fans, including down rods, safety hooks, motor assemblies, wiring, and matching multi-step speed wall regulators.
· Wall Fans: Supply and install Orient (Indian make) wall-mounted mechanical fans, complete with swivel-oscillation mechanisms, pull-cord or digital controls, mounting brackets, and local power connections.
· Exhaust Ventilation: Supply and install heavy-duty mechanical exhaust fans for all bathroom and laboratory spaces to ensure proper air changes. Laboratory units must be chemically resistant if specified by the layout.
7.20 [bookmark: _Toc235707054][bookmark: _Toc236854478][bookmark: _Toc238043254][bookmark: _Toc238382672][bookmark: _Toc239060051][bookmark: _Toc239061616]Air Conditioning and HVAC Infrastructure
· Window A/C Units: Supply and install O General Window brand (or approved equivalent) Freon air conditioning units in designated wall sleeves. Available in two capacities: 24,000 BTU and 18,000 BTU.
· Split A/C Units: Supply and install O General brand (or approved equivalent) split-type air conditioning units comprising indoor high-wall evaporators and outdoor condensing units. Available in two capacities: 24,000 BTU and 18,000 BTU.
· HVAC Connections and Drainage: All A/C installations must include structural mounting brackets, refrigerant copper piping insulated with elastomeric foam, interlocking control wiring, and a dedicated uPVC condensate drain pipe routed with a continuous downward slope connected to the nearest return water or greywater drainage point. 
[bookmark: _Toc236854479][bookmark: _Toc238043255][bookmark: _Toc238382673][bookmark: _Toc239060052][bookmark: _Toc239061617]Division  – Medical Waste Incinerator
7.21 [bookmark: _Toc236854480][bookmark: _Toc238043256][bookmark: _Toc238382674][bookmark: _Toc239060053][bookmark: _Toc239061618]General
The medical waste incinerator specified in the BOQ shall be suitable for treatment of infectious healthcare waste.
7.22 [bookmark: _Toc236854481][bookmark: _Toc238043257][bookmark: _Toc238382675][bookmark: _Toc239060054][bookmark: _Toc239061619]Combustion Requirements
Primary chamber:
· minimum 800°C.
Secondary chamber:
· minimum 1100°C.
Residence time:
· minimum 2 seconds.
7.23 [bookmark: _Toc236854482][bookmark: _Toc238043258][bookmark: _Toc238382676][bookmark: _Toc239060055][bookmark: _Toc239061620] Refractory Lining
High-alumina refractory brick:
· minimum thickness 114 mm.
Insulating layer:
· minimum 50 mm ceramic insulation.
7.24 [bookmark: _Toc236854483][bookmark: _Toc238043259][bookmark: _Toc238382677][bookmark: _Toc239060056][bookmark: _Toc239061621]Chimney
Material:
· stainless steel.
Height:
· Minimum 6 m above finished ground level.
7.25 [bookmark: _Toc236854484][bookmark: _Toc238043260][bookmark: _Toc238382678][bookmark: _Toc239060057][bookmark: _Toc239061622] Testing
The Contractor shall undertake:
· dry commissioning;
· operational commissioning;
· trial burn test;
· temperature verification.
7.26 [bookmark: _Toc235707707][bookmark: _Toc236854485][bookmark: _Toc238043261][bookmark: _Toc238382679][bookmark: _Toc239060058][bookmark: _Toc239061623]Construction of a Medical Waste Incinerator
7.27 [bookmark: _Toc235707710][bookmark: _Toc236854486][bookmark: _Toc238043262][bookmark: _Toc238382680][bookmark: _Toc239060059][bookmark: _Toc239061624]Technical Specifications
7.27.1 [bookmark: _Toc235707711][bookmark: _Toc236854487][bookmark: _Toc238043263][bookmark: _Toc238382681][bookmark: _Toc239060060][bookmark: _Toc239061625]Dimensions & Geometric Footprint
· Base Area Footprint: 2500 mm × 2500 mm overall outer dimension at ground level.
· Structural Vertical Height: 2720 mm overall height measured from the natural ground line to the concrete slab roof cap (excluding the vertical extension of the metal chimney).
· Operating Capacities: Designed as a natural-draught dual-chamber configuration with a nominal throughput capacity matching localized clinical demands (~12 to 15 kg/hour). 
7.27.2 [bookmark: _Toc235707712][bookmark: _Toc236854488][bookmark: _Toc238043264][bookmark: _Toc238382682][bookmark: _Toc239060061][bookmark: _Toc239061626]Civil & Concrete Substructure Works
· Mass Concrete Foundation: Cast an unreinforced or minimally reinforced structural foundation slab measuring 2500×2500 mm with an overall vertical thickness/depth of 650 mm.
· Concrete Strength Specification: Grade C20/25 nominal mix (1:2:4 ratio by volume) using pure Portland Cement, clean potable water, well-graded coarse aggregates (maximum aggregate size 20 mm), and washed river sand.
· Ash Pit Profile: Integrated directly below the primary combustion chamber, featuring smooth cement mortar rendering along internal faces to facilitate frictionless ash removal using long-handled scrapers.
· Concrete Access Steps: Monolithically cast concrete step structures provided at the designated loading bay face to afford operators an ergonomic, safe platform height during waste charging sequences.
7.27.3 [bookmark: _Toc235707713][bookmark: _Toc236854489][bookmark: _Toc238043265][bookmark: _Toc238382683][bookmark: _Toc239060062][bookmark: _Toc239061627]Masonry & Thermal Barrier Linings
· Primary Combustion Chamber Lining: Inner chamber surfaces exposed directly to active flames must be lined with premium refractory firebricks capable of withstanding continuous operational temperatures exceeding 850°C to 1100°C.
· Refractory Mortar Jointing: All firebricks must be laid exclusively with high-temperature refractory fireclay mortar (composed of premixed calcium-aluminate cement or specialized kaolin clays) with tight joints not exceeding 3 mm thickness.
· Exterior Protective Envelope: The outer structural walls above ground level shall be constructed using high-quality, well-burnt solid local clay bricks (1.5-brick thick layout configuration) laid in a highly workable 1:4 cement-to-sand mortar matrix, meticulously plumbed, joint-struck, and cured. 
7.27.4 [bookmark: _Toc235707714][bookmark: _Toc236854490][bookmark: _Toc238043266][bookmark: _Toc238382684][bookmark: _Toc239060063][bookmark: _Toc239061628]Metallurgical, Chimney & Metalwork Assemblies
· Exhaust Chimney Stack: Supply, fabricate, and install a vertical high-clearance exhaust chimney stack mounted securely through the top concrete roof slab.
· Material: Minimum 4 mm thick heat-resistant mild steel or stainless steel pipe.
· Diameter: Minimum 150 mm inside diameter (or as detailed on the approved UNOPS reference drawings).
· Height: The stack must rise to a minimum vertical clearance of 4 to 5 meters above the concrete slab cap to ensure proper natural draught and safe dispersion of emissions.
· Accessories: The chimney must be topped with an integrated conical rainwater cowl (spark arrestor) and rigidly anchored using high-tensile guy wires or welded structural steel support brackets to withstand local wind loads.
· Combustion Metal Grill (Grate): Fabricated using high-grade, heat-resistant cast iron or solid steel bars (minimum 20 mm diameter), spaced at 50 mm intervals center-to-center to endure intense thermal cycling without warping.
· Loading & Ash Clean-Out Doors: Formed from heavy-gauge, minimum 4 mm thick structural mild steel plates backed by dense ceramic fiber insulation blankets. Both doors must feature counterweighted hinge mechanisms and tight-fitting latches to ensure a complete, airtight secondary chamber seal.
7.28 [bookmark: _Toc235707110][bookmark: _Toc236854491][bookmark: _Toc238043267][bookmark: _Toc238382685][bookmark: _Toc239060064][bookmark: _Toc239061629]Execution, Workmanship, and Quality Control
· Refractory Curing Intermission: Following the completion of the firebrick masonry and refractory mortar lining, the structural shell must be allowed to dry naturally for at least 7 to 14 days. The contractor must then execute a controlled, slow-temperature wood-fire preheating phase to drive out residual moisture and cure the mortar bonds before full high-temperature operation.
· Metalwork Thermal Expansion: All internal structural steel supports, metal grills, and door frames must be installed with explicit expansion joints (minimum 10 mm to 15 mm clear gap packed with ceramic fiber rope) to prevent the steel from buckling or cracking the brickwork when expanding at high temperatures.
· Emissions and Draft Verification: The supervising engineer will conduct an initial operational trial run using standard test waste to verify that the mechanical charging doors lock tightly, the chimney stack draws exhaust smoothly without smoke backing out, and the ash pit doors maintain an airtight seal.
· Anti-Corrosion Painting: All external, non-insulated structural steel elements, door hinges, latch mechanisms, and the chimney stack base must be cleaned of mill scale and finished with two coats of high-temperature silicone-based aluminum paint capable of resisting temperatures up to 600°C.

[bookmark: _Toc238043268][bookmark: _Toc238382686][bookmark: _Toc239060065][bookmark: _Toc239061630]Appendix X: Handover Documentation and Final Deliverables
Upon completion of all rehabilitation works, the Contractor shall submit a complete set of handover documentation to the Engineer and the Employer. The submission shall demonstrate that all works have been executed, tested, commissioned, and completed in accordance with the Contract Documents, approved drawings, technical specifications, applicable standards, and the Engineer's instructions.
The Contractor shall be responsible for compiling, organizing, and submitting all required records and documents in both hard-copy and electronic formats. All documents shall be provided in clear, legible, and professionally organized form.
[bookmark: _Toc238043269][bookmark: _Toc238382687][bookmark: _Toc239060066][bookmark: _Toc239061631]As-Built Documentation
The Contractor shall prepare and submit comprehensive As-Built Drawings reflecting the actual works constructed on site. The drawings shall include, but not be limited to:
· Architectural layouts and modifications.
· Structural rehabilitation and repair works.
· Water supply systems and pipe networks.
· Sanitary and drainage systems.
· Septic tanks, manholes, inspection chambers, and related infrastructure.
· Electrical installations and distribution systems.
· HVAC systems, where applicable.
· Medical waste management facilities and incinerator installations, where applicable.
· External works and site infrastructure.
As-built drawings shall clearly indicate all deviations from the original design and shall be certified by the Contractor prior to submission.
[bookmark: _Toc238043270][bookmark: _Toc238382688][bookmark: _Toc239060067][bookmark: _Toc239061632]Testing and Commissioning Records
The Contractor shall submit complete testing and commissioning records for all installed and rehabilitated systems, including:
· Water supply network testing reports.
· Plumbing pressure testing reports.
· Drainage and sanitary system testing reports.
· Septic tank water-tightness testing reports.
· Electrical testing and commissioning reports.
· Earthing and electrical protection test certificates.
· Lighting performance and functional testing reports.
· HVAC commissioning records.
· Equipment start-up and operational testing reports.
· Medical waste incinerator commissioning and operational verification reports, where applicable.
All reports shall be signed by qualified personnel and approved by the Engineer.
[bookmark: _Toc238043271][bookmark: _Toc238382689][bookmark: _Toc239060068][bookmark: _Toc239061633]11.3 Quality Assurance and Quality Control Records
The Contractor shall submit all quality documentation generated during project implementation, including:
· Material approval records.
· Factory certificates and manufacturer's compliance certificates.
· Laboratory test reports.
· Inspection and approval records.
· Non-conformance reports and corrective actions undertaken.
· Quality checklists.
[bookmark: _Toc238043272][bookmark: _Toc238382690][bookmark: _Toc239060069][bookmark: _Toc239061634]11.4 Operation and Maintenance Manuals
The Contractor shall provide complete Operation and Maintenance (O&M) Manuals for all installed equipment, systems, and facilities.
The manuals shall include:
· Description of equipment.
· Manufacturer's data sheets.
· Operating procedures.
· Preventive maintenance requirements.
· Recommended maintenance schedules.
· Troubleshooting procedures.
· Spare parts lists.
· Safety precautions.
· Warranty information.
· Supplier and manufacturer contact details.
Manuals shall be provided in English and, where requested by the Employer, key operational instructions shall also be provided in Arabic.
[bookmark: _Toc238043273][bookmark: _Toc238382691][bookmark: _Toc239060070][bookmark: _Toc239061635]11.5 Training Requirements
Prior to final handover, the Contractor shall provide adequate training to hospital personnel designated by the Employer.
Training shall cover:
· Operation of water supply systems.
· Operation of electrical systems and distribution boards.
· Operation and maintenance of pumps and storage facilities.
· Use and maintenance of HVAC systems.
· Operation of medical waste incinerators and waste management facilities.
· Routine maintenance requirements for rehabilitated infrastructure.
Training records, attendance sheets, and training materials shall be submitted as part of the handover documentation.
[bookmark: _Toc238043274][bookmark: _Toc238382692][bookmark: _Toc239060071][bookmark: _Toc239061636]11.6 Warranties and Guarantees
The Contractor shall submit all warranties, guarantees, and manufacturer certifications associated with the completed works and supplied equipment.
These shall include:
· Equipment manufacturer's warranties.
· Waterproofing system warranties.
· Electrical installation warranties.
· Pump and mechanical equipment warranties.
· HVAC equipment warranties.
· Specialized system warranties required under the Contract.
Warranty periods shall commence from the date of Taking-Over Certificate issuance unless otherwise specified in the Contract.
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