SCOPE OF WORK (SOW) & TECHNICAL SPECIFICATIONS

Location: Tamboul Hospital, Al Jazira State, Sudan

SISSIRP – Rehabilitation and Upgrading of Tamboul Hospital

Contents

1. Introduction	7

2. General Requirements	7

2.1 Mobilization and Site Establishment	7

2.2 Verification of Existing Conditions	7

2.3 Hospital Operations and Infection Prevention	8

2.4 Health, Safety and Environmental Management	8

3. Demolition and Removal Works	9

4. Civil and Structural Rehabilitation Works	9

4.1 Concrete Works	9

4.2 Masonry Works	10

4.3 Structural Repairs	10

5. Roofing and Waterproofing Works	11

5.1 Roofing Works	11

5.2 Waterproofing Works	11

5.3 Roof Protection and Insulation	11

6. Doors, Windows and Metal Works	12

6.1 Doors	12

6.2 Windows	12

6.3 Metal Works	12

7. Plastering and Architectural Finishes	13

7.1 Plaster Works	13

7.2 Wall Finishes	13

7.3 Floor Finishes	13

7.4 Ceiling Works	14

7.5 Painting Works	14

8. Water Supply and Plumbing Works	14

8.1 Water Supply Network	14

8.2 Water Storage Systems	15

8.3 Booster Pump Systems	15

8.4 Plumbing Fixtures	15

9. Sanitary Sewerage and Drainage Works	16

9.1 Sanitary Sewer Network	16

9.2 Manholes and Inspection Chambers	16

9.3 Septic Tank Systems	16

9.4 Soakaway Systems	16

10. HVAC Works	17

10.1 Air Conditioning Systems	17

10.2 Ventilation Systems	17

10.3 Commissioning	17

11. Electrical Works	18

11.1 Power Distribution	18

11.2 Lighting Works	18

11.3 Socket Outlets and Power Services	18

11.4 Testing and Commissioning	19

12. Radiation Protection Works	19

13. Medical Waste Management Facilities	19

13.1 Civil Works	19

13.2 Incinerator Construction	20

13.3 Chimney System	20

13.4 Testing and Commissioning	20

14. External Works	20

14.1 Site Preparation	20

14.2 Roads, Walkways and Access	21

14.3 Boundary and Security Works	21

14.4 External Drainage	21

15. Oxygen Generation Plant Supply, Installation, Testing, Commissioning and Handover	22

16. Testing, Commissioning and Training	24

17. Handover Documentation and Final Deliverables	24

18. Defects Liability and Post-Completion Obligations	25

SECTION II: PROJECT TECHNICAL SPECIFICATIONS	26

Division 03: Concrete Works	26

General	26

Materials	26

Aggregates	26

Reinforcement	27

Concrete Strength	27

Testing	27

Execution, Workmanship, and Quality Control	28

Hot-Weather Concreting	28

General Requirements	28

Temperature Controls & Materials	28

Execution & Placement	29

Curing and Protection	29

2.1 Roof Slope Screed	29

2.2 Acrylic Waterproofing System	30

2.3 Flood Testing	30

3.1 Steel Doors	31

3.2 Finishing	31

3.3 Aluminum Windows	31

3.4	Technical Specifications	32

3.5	Pre-Installation Iron Framing	32

3.6	Passageways, Operation Rooms, and Bathrooms, Doors & Windows	32

3.7	Aluminum Skylight Assemblies	32

3.8	Ward Partitions	33

3.9	Execution, Workmanship, and Quality Control	33

3.10	Technical Specifications (Metal Works)	34

3.10.1	Security Grilles (Windows, Skylights, and Secondary Exterior Doors)	34

3.11	Staircase Handrails	34

3.12	Corrugated Iron Doors (Rooftop & Main Entrance doors)	34

3.12.1	Paint & Protective Finishes	35

3.13	Execution & Finishing Workmanship	35

4.	Plastering Technical Specifications	36

4.1	Material Requirements	36

4.2	Exterior Plastering (2 cm Thick)	36

4.3	Structural Crack Remediation Method	37

4.4	Execution, Workmanship, and Quality Control	37

5.	Division 09 – Finishes	38

5.1	Ceramic Wall Tiles	38

5.2	Porcelain Floor Tiles	38

5.3	Tile Testing	39

5.4	Technical Specifications (Tiling Works)	39

5.4.1	General Workmanship and Material Cutting	39

5.4.2	Porcelain Tiling (Rooms and Corridors)	39

5.4.3	Bathroom Ceramic Tiling	40

5.4.4	Natural Marble Works (Staircases and Entrances)	40

5.4.5	External Courtyard Tiling	41

5.5	Execution, Workmanship, and Quality Control	41

6.	Painting	41

1.1	Technical Specifications (Painting)	42

6.1.1 Material Standards and Approvals	42

6.1.2 Interior Walls Painting	42

6.1.3 Exterior Walls, Stairwells, and Parapet Walls Painting	43

6.1.4  Room and Corridor Ceilings Painting	43

6.1.5 Execution, Workmanship, and Quality Control	43

7	Technical Specifications (Epoxy)Material Requirements	44

7.2	Epoxy Application and Execution	44

7.3	Execution, Workmanship, and Quality Control	45

8	Division 22 – Water Supply and Plumbing	46

8.1	PPR Water Piping	46

8.2	Pipe Installation	46

8.3	Pressure Testing	47

8.4	Division 22.4 UPVC Drainage System	47

8.5	Sanitary Fixtures	47

8.6	Squat WC	47

8.7	Wash Basins	48

8.8	Division 22.6 Water Storage Tanks	48

8.9	Division 22.7 Booster Pumps	48

8.10	Division 22.8 Septic Tank Construction	49

8.11	Testing	49

8.12	Division 22.9 Soak-Away Pit	49

8.13	Division 23 – HVAC	49

8.13.1	Split Air Conditioning Units	49

8.13.2	Copper Pipework	50

8.14	Commissioning	50

9	Division 26  Electrical Works	50

9.1.1	Wiring	50

9.1.2	Distribution Boards	50

9.1.3	Earthing	51

9.1.4	Testing	51

9.2	Technical Specifications (Electrical Works)	51

9.3	Distribution Equipment and Switches	51

9.4	Lighting and Ventilation Systems	52

9.5	Air Conditioning and HVAC Infrastructure	52

10	Division  – Medical Waste Incinerator	53

10.1	General	53

10.2	Combustion Requirements	53

10.3	Refractory Lining	53

10.4	Chimney	54

10.5	Testing	54

10.6	Construction of a Medical Waste Incinerator	54

10.7	Technical Specifications	54

10.7.1	Dimensions & Geometric Footprint	54

10.7.2	Civil & Concrete Substructure Works	54

10.7.3	Masonry & Thermal Barrier Linings	55

10.7.4	Metallurgical, Chimney & Metalwork Assemblies	55

10.8	Execution, Workmanship, and Quality Control	56

Appendix X: Handover Documentation and Final Deliverables	64

X1. As-Built Documentation	65

X2. Testing and Commissioning Records	65

X.3 Quality Assurance and Quality Control Records	66

X.4 Operation and Maintenance Manuals	66

X.5 Training Requirements	67

X.6 Warranties and Guarantees	67

# 1. Introduction

The Works comprise the rehabilitation, repair, upgrading, construction, installation, testing, commissioning, and handover of selected hospital buildings, utility systems, support facilities, and associated infrastructure within Tamboul Hospital.

The objective of the project is to restore the operational functionality, structural integrity, public health standards, infection prevention measures, environmental health conditions, utility services, patient safety, and service delivery capacity of the hospital through integrated civil, architectural, mechanical, electrical, plumbing, sanitation, HVAC, and external infrastructure interventions.

The Contractor shall provide all labor, materials, plant, equipment, tools, temporary works, transportation, skilled and unskilled manpower, supervision, testing services, quality control resources, health and safety provisions, and all incidental works necessary for the complete execution and successful completion of the Works.

# 2. General Requirements

## 2.1 Mobilization and Site Establishment

The Contractor shall:

- Mobilize personnel, construction equipment, materials, and site resources.

- Establish temporary site offices, stores, workshops, and worker welfare facilities.

- Install project signboards and safety signage.

- Provide temporary water and power supplies required for construction activities.

- Establish temporary fencing, barriers, and security arrangements.

- Implement access control measures and traffic management procedures.

- Maintain site security throughout the construction period.

- The Contractor shall engage a qualified Civil Engineer and (other specialties to be added as needed) to supervise and oversee the execution of the relevant works throughout the project implementation

## 2.2 Verification of Existing Conditions

Before commencement of construction activities, the Contractor shall:

- Verify dimensions, levels, and existing building conditions.

- Confirm all utility routes and service connections.

- Verify structural and architectural conditions.

- Confirm locations of existing buried services.

- Verify all quantities and site conditions relevant to the Works.

Any discrepancies identified between actual site conditions and tender documents shall immediately be reported to the Engineer.

## 2.3 Hospital Operations and Infection Prevention

As parts of the hospital may remain operational during implementation, the Contractor shall:

- Develop work phasing plans for approval.

- Maintain uninterrupted access to essential healthcare services.

- Implement Infection Prevention and Control (IPC) measures.

- Install dust-control barriers and temporary partitions.

- Manage noise and vibration.

- Protect existing medical equipment and healthcare assets.

- Maintain emergency access routes at all times.

- Segregate construction activities from clinical operations.

- Prevent contamination of occupied healthcare areas.

## 2.4 Health, Safety and Environmental Management

The Contractor shall prepare and implement:

- Site-Specific Health and Safety Plan.

- Environmental Management Plan.

- Waste Management Plan.

- Emergency Response Plan.

- Traffic Management Plan.

- Incident Reporting Procedures.

The Contractor shall provide adequate personal protective equipment and ensure compliance with all applicable health, safety, environmental, and labor requirements.

# 3. Demolition and Removal Works

The Contractor shall undertake all demolition, dismantling, removal, stripping, disposal, and preparatory works required for the rehabilitation activities including:

- Removal of damaged roofing sheets.

- Removal of deteriorated waterproofing systems.

- Removal of defective ceilings.

- Removal of damaged tiles.

- Removal of damaged plastering and wall finishes.

- Removal of deteriorated paint systems.

- Removal of damaged doors and windows.

- Removal of obsolete plumbing systems and sanitary fixtures.

- Removal of defective drainage systems.

- Removal of damaged electrical accessories and fittings.

- Removal of deteriorated metal works.

- Removal of abandoned services and installations.

- Removal and disposal of construction debris.

Demolition works shall be executed carefully to avoid damage to adjacent structures and ongoing hospital operations.

# 4. Civil and Structural Rehabilitation Works

The Contractor shall undertake civil and structural rehabilitation works for all hospital buildings identified in the BOQ, including wards, treatment units, support facilities, laboratories, administration areas, service blocks, utility facilities, and associated structures.

## 4.1 Concrete Works

The Works shall include:

- Reinforced concrete foundations.

- Mass concrete works.

- Pump bases and equipment foundations.

- Reinforced concrete covers and slabs.

- Concrete manholes.

- Septic tank construction.

- Soakaway structures.

- Concrete repair works.

- Ramp construction.

- Walkway construction.

- Concrete plinths and supports.

## 4.2 Masonry Works

The Contractor shall execute:

- Construction of masonry walls.

- Rehabilitation of damaged blockwork.

- Rehabilitation of brick masonry.

- Partition wall construction.

- Openings modifications.

- Boundary wall works.

- Incinerator masonry structures.

- Associated masonry repairs.

## 4.3 Structural Repairs

Works shall include:

- Crack repairs.

- Structural strengthening works.

- Concrete rehabilitation.

- Lintel repairs.

- Reinforcement protection and repairs.

- Local structural modifications.

- Rehabilitation of deteriorated structural components.

# 5. Roofing and Waterproofing Works

## 5.1 Roofing Works

The Contractor shall:

- Remove damaged roofing materials.

- Repair roof support structures.

- Supply and install new galvanized roofing sheets.

- Install ridge caps and accessories.

- Install flashings and roof trims.

- Repair roof drainage components.

## 5.2 Waterproofing Works

The Works shall include:

- Roof slope correction screeds.

- Acrylic waterproofing systems.

- Waterproof membranes.

- Surface preparation works.

- Waterproof sealing of joints and penetrations.

- Flood testing and leakage testing.

## 5.3 Roof Protection and Insulation

The Contractor shall provide all roof protection measures required to ensure long-term performance of rehabilitated roofs.

# 6. Doors, Windows and Metal Works

## 6.1 Doors

The Contractor shall supply and install:

- Steel doors.

- Aluminum-framed doors.

- Corrugated iron doors.

- Specialized hospital doors.

- Radiation-protection doors where required.

- Door frames.

- Hardware and accessories.

- Locks, handles, hinges, and closers.

## 6.2 Windows

The Contractor shall supply and install:

- Aluminum windows.

- Security-screened windows.

- Replacement glazing.

- Window accessories and ironmongery.

- Window rehabilitation works.

## 6.3 Metal Works

The Works shall include:

- Security grilles.

- Stair handrails.

- Protective guards.

- Expanded metal screens.

- Fabricated steel works.

- Steel supports and brackets.

- Miscellaneous metal fabrication works.

# 7. Plastering and Architectural Finishes

## 7.1 Plaster Works

The Contractor shall perform:

- Internal plastering.

- External plastering.

- Repair of cracked surfaces.

- Structural crack treatment using expanded metal mesh reinforcement.

- Surface leveling.

- Preparation for painting.

## 7.2 Wall Finishes

The Works shall include:

- Ceramic wall tile installation.

- Hygiene-sensitive finishes.

- Moisture-resistant wall treatments.

- Protective wall finishes for healthcare environments.

## 7.3 Floor Finishes

The Contractor shall provide:

- Porcelain floor tiles.

- Ceramic floor tiles.

- Skirting works.

- External paving tiles.

- Floor leveling and preparation.

- Epoxy flooring in designated healthcare areas.

## 7.4 Ceiling Works

The Contractor shall provide:

- Suspended ceilings.

- Ceiling repairs.

- Ceiling framing.

- Access panels.

- Ceiling finishing and painting.

## 7.5 Painting Works

The Contractor shall apply:

- Interior acrylic paint systems.

- External weather-resistant paint systems.

- Ceiling paints.

- Protective coatings.

- Metal painting systems.

- Surface preparation, priming, and finishing coats.

# 8. Water Supply and Plumbing Works

## 8.1 Water Supply Network

The Contractor shall rehabilitate and upgrade the hospital water distribution system including:

- PPR piping systems.

- Pipe fittings and accessories.

- Valves and controls.

- Connections to existing networks.

- Pipe supports and anchorage.

- Hydrostatic testing.

## 8.2 Water Storage Systems

The Contractor shall provide:

- Water storage tanks.

- Tank support structures.

- Pipework connections.

- Overflow and drainage systems.

- Tank accessories.

## 8.3 Booster Pump Systems

The Contractor shall supply, install, test, and commission:

- Booster pumps.

- Control panels.

- Associated valves and fittings.

- Pump foundations.

- Electrical connections.

## 8.4 Plumbing Fixtures

The Contractor shall supply and install:

- Water closets.

- Squatting toilets.

- Wash hand basins.

- Faucets.

- Traps.

- Shower fittings.

- Plumbing accessories.

- Associated pipework connections.

# 9. Sanitary Sewerage and Drainage Works

## 9.1 Sanitary Sewer Network

The Works shall include:

- New underground sewer networks.

- Internal drainage systems.

- Waste and vent networks.

- House connections.

- Testing and commissioning.

## 9.2 Manholes and Inspection Chambers

The Contractor shall construct and rehabilitate:

- Inspection chambers.

- Sewer manholes.

- Covers and frames.

- Channeling and benching works.

## 9.3 Septic Tank Systems

The Contractor shall construct reinforced concrete septic tanks including:

- Excavation.

- Concrete works.

- Waterproofing.

- Internal partitions.

- Access covers.

- Ventilation systems.

- Pipework connections.

## 9.4 Soakaway Systems

The Contractor shall construct soakaway pits including:

- Excavation works.

- Masonry or concrete lining.

- Graded filter media.

- Covers and access openings.

- Testing prior to handover.

# 10. HVAC Works

The Contractor shall supply, install, test, and commission HVAC systems including:

## 10.1 Air Conditioning Systems

- Split air-conditioning units.

- Indoor and outdoor units.

- Inverter systems.

- Copper refrigerant piping.

- Insulation systems.

- Condensate drainage.

- Electrical connections.

## 10.2 Ventilation Systems

- Exhaust fans.

- Wall-mounted fans.

- Ceiling fans.

- Mechanical ventilation systems.

- Air circulation devices.

## 10.3 Commissioning

The Contractor shall carry out:

- Pressure testing.

- Vacuum testing.

- Refrigerant verification.

- Operational performance testing.

- User training.

# 11. Electrical Works

## 11.1 Power Distribution

The Contractor shall rehabilitate and upgrade electrical systems including:

- Main distribution boards.

- Sub-distribution boards.

- Circuit breakers.

- Earthing systems.

- Cabling.

- Conduits.

- Support systems.

- Protective devices.

## 11.2 Lighting Works

The Works shall include:

- Internal lighting systems.

- External lighting systems.

- Healthcare lighting fixtures.

- Moisture-resistant lighting.

- Emergency lighting where indicated.

## 11.3 Socket Outlets and Power Services

The Contractor shall install:

- General power outlets.

- Dedicated outlets.

- Equipment connections.

- A/C power supplies.

- Isolators and switches.

## 11.4 Testing and Commissioning

The Contractor shall conduct:

- Continuity testing.

- Insulation resistance testing.

- Earth resistance testing.

- Functional testing.

- System commissioning.

# 12. Radiation Protection Works

Where identified within radiology and diagnostic facilities, the Contractor shall provide:

- Lead-lined doors.

- Lead protection assemblies.

- Radiation shielding components.

- Protection of walls and openings.

- Compliance testing and verification.

# 13. Medical Waste Management Facilities

The Contractor shall construct and commission a medical waste incinerator including:

## 13.1 Civil Works

- Excavation.

- Foundations.

- Concrete works.

- Masonry works.

- Access structures.

- Ash pit construction.

## 13.2 Incinerator Construction

- Primary combustion chamber.

- Secondary combustion chamber.

- Refractory lining.

- Loading doors.

- Ash removal systems.

- Structural metal components.

## 13.3 Chimney System

- Stainless steel chimney.

- Chimney supports.

- Rain cap.

- Emission discharge arrangements.

## 13.4 Testing and Commissioning

The Contractor shall perform:

- Dry commissioning.

- Trial burn tests.

- Temperature verification.

- Operational testing.

- Handover training.

# 14. External Works

## 14.1 Site Preparation

The Contractor shall carry out:

- Clearing and cleaning.

- Excavation and backfilling.

- Site grading.

- Surface reinstatement.

## 14.2 Roads, Walkways and Access

The Works shall include:

- Walkways.

- Pedestrian access routes.

- Accessibility ramps.

- Surface restoration.

- Connection pathways.

## 14.3 Boundary and Security Works

The Contractor shall execute:

- Boundary wall rehabilitation.

- New boundary wall works where indicated.

- Gate construction and repairs.

- Security improvements.

## 14.4 External Drainage

The Contractor shall provide:

- Surface drainage improvements.

- Drainage channels.

- Runoff management measures.

- Connections to site drainage systems.

# 15. Oxygen Generation Plant Supply, Installation, Testing, Commissioning and Handover

The Contractor shall design, supply, deliver, install, test, commission, and hand over a complete turnkey Pressure Swing Adsorption (PSA) Medical Oxygen Generation Plant at the designated hospital site. The system shall be fully operational and capable of producing medical-grade oxygen for continuous cylinder filling operations and shall include all equipment, materials, accessories, civil interfaces, mechanical and electrical works, safety provisions, training, documentation, and ancillary components necessary for full functionality and reliable long-term operation.

The oxygen generation plant shall comply with ISO 80601-2-69 and all applicable international standards for medical oxygen production systems. The system shall be designed for continuous twenty-four (24) hour operation under local environmental conditions and shall maintain full performance at ambient temperatures up to +55°C. The Contractor shall ensure that the oxygen plant, compressors, dryers, and associated auxiliary equipment are adequately protected from dust ingress, solar heat gain, and adverse environmental conditions through the designated building and associated protective measures.

The scope of work shall include, but not be limited to, the following:

- Supply and installation of a complete PSA oxygen generation plant with a minimum production capacity of 40 Nm³/hour.

- Oxygen purity of 93% ±3%.

- Capability to fill approximately 50 to 70 oxygen cylinders per day.

- Cylinder filling pressure ranging from 150 to 200 bar.

- Air compressors, air treatment systems, dryers, filters, receiver tanks, oxygen generator units, oxygen storage vessels, booster compressor, filling manifold system, interconnecting piping, valves, and all associated accessories.

- PLC/HMI-based monitoring and control system for operation, performance monitoring, fault detection, and alarm management.

- Oxygen analyzer, safety alarms, emergency shutdown systems, and all required instrumentation.

- Testing, calibration, commissioning, performance verification, and demonstration of compliance with specified operational requirements.

The Contractor shall undertake a complete assessment of the oxygen plant electrical load requirements and shall provide all electrical systems necessary for the safe and reliable operation of the facility. Electrical works shall include, but not be limited to:

- Preparation of load calculations and electrical design.

- Supply and installation of a dedicated main distribution board for the oxygen plant.

- Motor starters, protection devices, isolators, and control panels.

- Earthing and bonding systems.

- Power and control cabling.

- Internal equipment wiring and connections.

- Surge protection devices.

- Cable containment and accessories.

- Testing, inspection, and commissioning of all electrical installations.

All electrical works shall comply with applicable national electrical regulations, recognized engineering standards, and manufacturer recommendations.

Prior to procurement and equipment manufacture, the Contractor shall submit for approval detailed shop drawings, equipment data sheets, process flow diagrams, electrical single-line diagrams, equipment layouts, and all other relevant technical documentation.

The Contractor shall also provide:

- Firefighting equipment and fire safety provisions appropriate for the oxygen generation facility.

- Emergency shutdown arrangements and emergency response procedures.

- Full compliance with Environmental, Health, Safety, and Social (EHSS) requirements throughout implementation and operation.

- An Operations and Maintenance (O&M) Plan including preventive maintenance schedules and recommended maintenance procedures.

- A six (6) month supply of essential spare parts and consumables.

- Comprehensive operation and maintenance training for a minimum of ten (10) designated staff members.

- Factory, site acceptance, and performance testing documentation.

- As-built drawings, operation manuals, maintenance manuals, warranties, certificates, and commissioning reports.

The Contractor shall remain responsible for the satisfactory performance of the oxygen generation plant during a Defects Liability Period (DLP) of not less than twelve (12) months following commissioning and handover. The supplied equipment shall be covered by a minimum twenty-four (24) month manufacturer's warranty. Any defects, failures, or deficiencies identified during the warranty and DLP periods shall be rectified by the Contractor at no additional cost to the Employer.

The works shall be completed on a turnkey basis, and any equipment, materials, services, or accessories not explicitly listed but required for safe, reliable, and fully functional operation of the oxygen generation plant shall be deemed included within the Contractor's scope and contract price.

# 16. Testing, Commissioning and Training

The Contractor shall perform complete testing, commissioning, adjustment, balancing, demonstration, and training for all systems, equipment, and infrastructure installed under the Contract.

Training shall be provided for hospital staff covering:

- Water systems.

- Electrical systems.

- HVAC systems.

- Plumbing systems.

- Wastewater systems.

- Medical waste incinerator operation.

- Routine maintenance procedures.

# 17. Handover Documentation and Final Deliverables

Prior to final acceptance, the Contractor shall submit:

- As-built drawings.

- Operation and Maintenance Manuals.

- Test certificates.

- Commissioning reports.

- Product data sheets.

- Material approval records.

- Warranty certificates.

- Training records.

- Spare parts lists.

- Preventive maintenance schedules.

# 18. Defects Liability and Post-Completion Obligations

The Contractor shall remain responsible during the Defects Liability Period for:

- Correction of defects.

- Replacement of defective materials.

- Rectification of workmanship deficiencies.

- Resolution of operational deficiencies attributed to the Works.

- Compliance with all warranty obligations.

The Works shall be considered complete only after successful testing and commissioning, submission of all handover documentation, correction of all defects, and issuance of the Taking-Over Certificate by the Employer.

# SECTION II: PROJECT TECHNICAL SPECIFICATIONS

To Be Read Together with the SISSIRP Unified Technical Specifications.

"To be read in conjunction with the SISSIRP Unified Technical Specifications. In case of discrepancies between the unified specifications and item-specific descriptions, the provisions of this document shall prevail, subject to the approval of the IOM Engineer."

## Division 03: Concrete Works

### General

Concrete works shall include all reinforced concrete elements required under the rehabilitation works, including:

- Roof screeds.

- Water tank supports.

- Pump foundations.

- Manholes.

- Septic tank structures.

- Soak-away structures.

- Access slabs.

- Stair repairs.

- Structural rehabilitation works.

### Materials

#### Cement

- Ordinary Portland Cement shall comply with:

- ASTM C150 Type I

- BS EN 197-1

- Sudanese standards where applicable.

Cement older than three months from the date of manufacturing shall not be used.

### Aggregates

Aggregates shall comply with ASTM C33.

Maximum aggregate size:

- 20 mm for reinforced concrete.

- 10 mm for repair works and toppings.

### Reinforcement

High-yield deformed bars:

- fy = 460 MPa minimum.

Steel shall be free from:

- oil

- mud

- loose rust

- paint

## Concrete Strength

| Application | Minimum Strength |
| --- | --- |
| Blinding | C15 |
| Manholes | C20 |
| Septic tanks | C25 |
| Structural repair works | C25 |
| Water tank supports | C25 |

## Testing

The Contractor shall provide:

- Slump test for every pour.

- Six concrete cubes for every 50 m³.

- 7-day and 28-day compressive strength tests.

- Crushing Reports: All data provided by the independent testing facility must log the failure load in Kilonewtons (kN), the surface area of the test specimen in square millimeters (mm²), and the final calculated strength converted precisely into N/mm².

- Non-Compliance: Any sample batch registering a crushing strength below 30 N/mm² at the 28-day interval will be flagged as a structural failure, prompting immediate halting of subsequent works and mandatory core-testing.

## Execution, Workmanship, and Quality Control

- Mechanical Compaction: Immediately following placement, all fresh concrete must be thoroughly compacted around the steel reinforcement mesh using mechanical needle vibrators to eliminate air pockets, honeycombing, and voids.

- Curing Requirements: Exposed concrete surfaces must be kept continuously damp via continuous water spraying or ponding system to ensure slow hydration and prevent shrinkage cracks until the 30 N/mm² design strength is achieved.

- Engineering Clearance: No concrete pouring shall begin until the supervising engineer checks and signs off on the formwork alignment, rigid bracing, cleanliness, and structural steel reinforcement spacing.

## Hot-Weather Concreting

### General Requirements

- Standard Compliance: All concrete works executed during hot weather conditions shall strictly comply with the technical frameworks of BS EN 206 and BS 8500.

- Applicability: This clause applies to all in-situ concrete works irrespective of individual element volume or mix.

### Temperature Controls & Materials

- Concrete Discharge Temperature: The temperature of fresh concrete at the point of discharge shall not exceed 35°C, unless specialized, engineer-approved cooling measures are implemented.

- Cement Storage and Delivery Temperature: Cement powder at the time of mixing shall not exceed 80°C. Bagged cement must be stored in a shaded, well-ventilated weatherproof structure, elevated off the ground, and protected from direct solar heat gain to prevent flash setting and thermal cracking.

- Pre-cooling Measures: The Contractor shall utilize chilled batch water, flake ice, or shaded aggregate stockpiles to maintain the specified temperature thresholds.

### Execution & Placement

- Substrate Preparation: Formwork, reinforcement, and subgrades shall be thoroughly pre-wetted with cool water immediately prior to placement to prevent the rapid absorption of mix water.

- Scheduling Restrictions: Concrete placement shall be rescheduled to cooler periods of the day (early morning or night) if ambient temperatures jeopardize setting times or workability.

- Delivery Timeframes: Transit and waiting times for ready-mix concrete delivery trucks shall be minimized to prevent premature slump loss.

### Curing and Protection

- Initial Curing: Curing operations must commence immediately following final finishing preventing plastic shrinkage cracking caused by high evaporation rates.

Method & Duration: Continuous wet curing (moist burlap/ponding) or approved chemical curing membranes shall be maintained for a minimum of 7 consecutive days.

2. Division 07 –Waterproofing and Roof Protection

## 2.1 Roof Slope Screed

Roof screed (Khafjah) indicated in the BOQ shall:

- Achieve minimum slope of 1:40;

- Use cement: sand ratio of 1:3;

- have minimum thickness of 40 mm at high points;

- Contain waterproofing admixture approved by the Engineer.

- The surface shall be free from ponding after completion.

- Maximum standing water after rainfall is 5 mm.

## 2.2 Acrylic Waterproofing System

The acrylic waterproofing system referenced in the BOQ shall be equivalent to:

- Mixguard AC,

- SikaTop Seal 107,

- Ceresit CR166, or

- Approved equivalent.

Properties:

- Crack bridging.

- Flexible.

- UV resistant.

- Suitable for Sudan climate.

Application:

- Minimum two coats.

- Total dry film thickness not less than 2 mm.

## 2.3 Flood Testing

Completed waterproofed areas shall undergo:

- 72-hour ponding test.

Acceptance Criteria:

- No leakage;

- No dampness;

- No visible deterioration.

  - Division 08 – Doors, Windows and Metal Works

## 3.1 Steel Doors

Steel doors shall comprise:

Frame

- RHS 40 × 80 × 2 mm.

- Fully welded.

Door Leaf

- RHS 30 × 60 × 2 mm.

- 1.2 mm minimum steel sheet.

- Internal stiffeners at maximum 400 mm spacing.

## 3.2 Finishing

All steelwork shall receive:

- One zinc-rich primer coat;

- Two anti-rust coats;

- Two enamel finishing coats.

Dry film thickness:

- Minimum 100 microns.

## 3.3 Aluminum Windows

Aluminum sections shall:

- Minimum 1.4 mm thickness;

- Powder-coated finish;

- 60–80 micron coating thickness.

Glass:

- Minimum 6 mm clear glazing.

## Technical Specifications

### Pre-Installation Iron Framing

- Material Profile: High-tensile structural steel rectangular hollow sections (RHS) measuring 80mm × 40mm (8cm × 4cm).

- Treatment: Shop-applied anti-corrosive red-oxide primer layer before structural installation into masonry surrounds.

### Passageways, Operation Rooms, and Bathrooms, Doors & Windows

- Aluminum Extrusions: Genuine Saudi aluminum architectural profiles featuring a 2mm material wall thickness.

- Glazing (Glass Panels): 6mm thick, tempered or high-strength architectural tinted glass, set with premium EPDM rubber gaskets.

- Hardware & Accessories:

  - Heavy-duty commercial hydraulic door closers configured with adjustable latching speeds.

  - Stainless steel institutional handles, heavy-gauge commercial locksets, and perimeter trim.

  - Heavy-duty ball-bearing sliding track assemblies for the operation room doors.

- Size Variations (Doors):

  - Standard Passageway/Zone Doors: 2.0m × 2.2m | 2.7m × 2.2m | 1.4m × 2.2m | 1.0m × 2.2m | or as in BOQ.

  - Bathroom Doors: 0.80m × 2.2m

  - Operation Room Doors (Sliding Type): 1.5m × 2.2m

- Size Variations (Windows):

  - Standard Architectural Windows: 1.4m × 1.8m | 3.0m × 2.0m | or as in BOQ

### Aluminum Skylight Assemblies

- Structural Frame: Built from 2mm thick aluminum profiles matching the performance properties of structural windows.

- Glazing: Weatherproof, high-impact 6mm tinted safety glass featuring UV-resistant commercial perimeter sealants.

- Size Variations (Skylights):

  - Staircase Skylights: 0.80m × 1.2m

  - Corridor/Zone Skylights: 0.40m × 2.0m

  - Bathroom Skylights: 0.60m × 0.60m

### Ward Partitions

- Profile System: Aluminum structural sections featuring a heavy 4mm profile wall thickness.

- Assembly Elements: Supplied complete with institutional floor/wall fixing bolts, internal privacy panels/glazing, structural connectors, and heavy-duty handles.

## Execution, Workmanship, and Quality Control

- On-Site Dimensions: The contractor must verify all structural opening sizes on-site prior to completing factory assembly of the aluminum frames. No spacing gaps greater than 5 mm between the steel sub-frame and aluminum frame are permitted.

- Glazing Standards: All 6 mm tinted glass panels must be set inside the aluminum channels using continuous, high-grade EPDM rubber gaskets. Silicone sealants must be applied cleanly along the external perimeter to ensure absolute wind and water tightness.

- Plumb and Level Tolerances: Erect all frames perfectly vertical and level. The maximum allowable installation deviation is 1 mm per meter of height. Diagonal measurements of completed frames must be identical to guarantee perfect squareness.

- Hardware Adjustment: Adjust all automatic door closers and sliding tracks so that doors operate smoothly without requiring excessive force, and latch securely without rattling.

- Protection and Cleaning: Keep all protective factory plastic wrap on the aluminum profiles until final handover. Clean away all structural mortar, plaster splashes, or silicone streaks from the glass and metal surfaces using non-abrasive, non-acidic cleaning agents.

## Technical Specifications (Metal Works)

    - Security Grilles (Windows, Skylights, and Secondary Exterior Doors)

- External Perimeter Frame: Heavy-duty, structural steel rectangular hollow section (RHS) pipes measuring 80mm × 40mm (minimum wall thickness 2.0mm).

- Internal Vertical Elements: Structural steel RHS pipes measuring 60mm × 30mm, arrayed vertically with a maximum clear spacing of 200mm center-to-center.

- Internal Horizontal Elements: Structural steel RHS pipes measuring 80mm × 40mm, positioned horizontally every 700mm to form a rigid geometric pentagonal pattern.

- Fastening Hardware: Heavy-duty tamper-proof masonry expansion bolts or chemically anchored steel pins driven at least 80mm deep into concrete structural surrounds.

  - Staircase Handrails

- Material Composition: Industrial-grade stainless steel (Grade 304 or higher) or heavy-gauge galvanized structural steel pipe profiles.

- Dimensions: Ergonomic top rail diameter between 38mm and 50mm, positioned at a finished height of 900mm to 1000mm measured vertically from the stair tread nosing.

- Structural Supports: Fixed stanchions/posts spaced at a maximum interval of 1200mm, firmly anchored directly into the structural concrete staircase base plates or side walls.

  - Corrugated Iron Doors (Rooftop & Main Entrance doors)

- Rooftop Staircase Door (1.0m × 2.2m):

  - Skin: Heavy-gauge, weather-resistant galvanized corrugated iron sheeting (minimum 1.2mm thickness) welded to a rigid internal square structural steel chassis.

  - Hardware: Weatherproof, heavy-duty commercial mortise locksets, stainless steel pull handles, and a minimum of three heavy-duty bullet hinges.

- Main Entrance Door (3.0m × 2.2m):

  - Configuration: Double-leaf structural iron gate matching the 2.2-meter clearance, constructed from high-tensile corrugated iron sheets integrated with structural internal bracing.

  - Hardware: Heavy-duty industrial slide bolts (top and bottom drop-bolts), high-security institutional padlock eyes, commercial pull bars, and structural-grade pivoting hinges.

    - Paint & Protective Finishes

- Primer Base: Minimum of two (2) separate coats of high-performance zinc-chromate or red-oxide anti-corrosive structural metal primer.

- Finish Coat: Minimum of two (2) coats of premium poly-urethane or industrial-grade gloss enamel paint designed for heavy UV exposure and frequent chemical washing.

## Execution & Finishing Workmanship

- Welding: All structural joints must be fully, continuously welded (no spot welding allowed). All welds must be ground smooth, flush, and free of slag or pinholes before painting.

- Plumb & Square Alignment: Install all doors, security frames, and handrails perfectly true, level, and vertically plumb, holding tolerances within a strict ±2mm variance.

- Ergonomic Safety: Ensure all staircase handrail terminations are cleanly returned smooth into the structural wall surface or dropped down to the floor to prevent clothing snags.

- Anti-Corrosion Priming: All steel surfaces must be thoroughly de-rusted, degreased, and treated with at least two coats of zinc-phosphate anti-corrosive primer before leaving the fabrication workshop.

- Tolerances: Frames must be installed strictly plumb and square. Maximum allowable deviation across structural heights is ±2 mm.

- Supervising Engineer Approval: Present the final installed grilles, handrails, and entrance assemblies for close joint inspection and official written sign-off.

# Plastering Technical Specifications

## Material Requirements

- Cement: Premium-quality Ordinary Portland Cement (OPC) free from lumps, moisture, or premature setting.

- Sand: Clean, sharp, well-graded fine river sand, screened to remove clay, loam, shells, organic particles, or chemical impurities.

- Expanded Metal Mesh (Expanda): High-tensile, corrosion-resistant galvanized expanded steel mesh sheet with a minimum width of 30 cm to 40 cm.

- Water: Fresh, potable, clean, and completely free from harmful oils, acids, alkalis, or organic matter.

## Exterior Plastering (2 cm Thick)

- Application Areas: Exterior walls, inner and outer faces of the roof parapets, and all faces of the stairwell structure.

- Mix Ratio: Strictly 1:6 by volume (1 part cement to 6 parts screened sand).

- Thickness: Applied to a uniform, flat, and plumb total thickness of 2 cm.

- Finish Style: Perfectly smooth, level surface achieved via timber floats and steel trowels. No trowel marks, waves, or surface ripples are permitted.

- Tight Area Integration: Plaster neatly flush up to external electrical junction boxes, switches, and utility fixtures. Maintain sharp, square, orthogonal corners without any messy over-spill.

## Structural Crack Remediation Method

- Plaster Removal: Chip away and entirely remove the failing, cracked plaster down to the bare red brick masonry substrate. The removal strip must expose at least 15 cm to 20 cm (150–200 mm) of clean masonry on both left and right sides of the crack line.

- Surface Cleaning: Brush away loose dust, mortar fragments, and debris from the exposed masonry channel, then moisten the surface thoroughly.

- Mesh Installation: Position and securely fasten the expanded metal mesh (Expanda) centrally over the crack using galvanized masonry nails or pins. The mesh must extend a minimum of 150 mm to 200 mm past the crack boundary on both sides to distribute tensile stresses.

- Replastering: Apply a primary bonding coat, followed by the finishing plaster coat, ensuring the new surface matches the plane, texture, and level of the surrounding existing plaster perfectly.

## Execution, Workmanship, and Quality Control

- Scaffolding Safety: Erect independent, rigid external tubular scaffolding fitted with secure working platforms, toe boards, and catch nets along the building perimeter.

- Engineering Sign-off: Do not apply mesh or plaster over cracked zones until the supervising engineer inspects the cleaned masonry substrate and approves the structural preparation.

- Water Curing: Keep all newly applied exterior plaster and repaired crack patches continuously damp by spraying with water at least twice daily for a minimum period of 7 days post-construction to ensure proper hydration and prevent shrinkage cracks.

- Weather Restrictions: Do not apply cement plaster during heavy rain, high winds, or ambient temperatures exceeding 40°C to avoid premature drying or wash-outs.

# Division 09 – Finishes

## Ceramic Wall Tiles

Applicable to:

- toilets;

- bathrooms;

- wash areas;

- sanitary rooms.

Requirements:

- Water absorption ≤ 3%.

- Minimum thickness 8 mm.

Installation:

- Cement adhesive C2 grade.

- Joint width 2–3 mm.

## Porcelain Floor Tiles

Porcelain tiles shall be:

- Fully vitrified;

- Water absorption <0.5%;

- Minimum thickness 10 mm.

Slip resistance:

- R10 minimum.

Wet areas:

- R11 minimum.

## Tile Testing

Lippage:

- maximum 1 mm.

Hollow sounding areas:

- maximum 5% of room area.

Defective tiles shall be replaced.

## Technical Specifications (Tiling Works)

### General Workmanship and Material Cutting

- Edge Precision: All tile cutting must be done using professional wet-saw mechanical cutters to ensure perfectly straight, crisp, unchipped edges. Hand-snapping or jagged manual cuts are strictly prohibited.

- Grouting & Expansion: All joints must be fully packed with a uniform slurry of premium white cement or an approved color-matched grout. Any excess grout must be wiped clean with a damp sponge before it sets.

- Layout Symmetry: Tile layouts must be planned from the center of each room or corridor to ensure balanced, equal-sized cut tiles along the perimeter boundaries.

### Porcelain Tiling (Rooms and Corridors)

- Flooring: Supply and install premium-grade 60 × 60 cm porcelain tiles. Tiles must be bedded on a true-to-level layer of 1:4 cement mortar (1 part cement to 4 parts dry sand). Surfaces must be checked continuously with a spirit level to ensure a completely flat finish with zero lippage.

- Skirting: Supply and install matching porcelain skirting boards cut to a uniform height of 10 cm along all room and corridor perimeters. Skirting must be installed perfectly flush or with a uniform protrusion as approved by the engineer, with top edges smoothly grouted.

### Bathroom Ceramic Tiling

- Bathroom Floors: Supply and install high-quality Egyptian ceramic tiles measuring 30 × 30 cm. These must be bedded on a 1:4 cement mortar mix. The installer must maintain a strict, uniform slope falling toward the floor drainage traps to guarantee that no water ponds on the floor.

- Bathroom Walls: Supply and install matching Egyptian ceramic wall tiles measuring 50 × 30 cm. Tiles must be fixed perfectly plumb using a thin-set mortar or approved tile adhesive over a rough plaster scratch coat, maintaining perfectly aligned horizontal and vertical grout lines.

### Natural Marble Works (Staircases and Entrances)

- Internal Staircase Steps: Supply, cut, and install premium natural marble slabs for the internal staircase steps. The steps must feature a clear width of 1.0 meter, incorporating both the horizontal treads and vertical risers. Slabs must be selected for uniform color, pattern, and grain continuity.

- Internal Staircase Landings: Supply and install matching natural marble slabs for the internal staircase landing zones, ensuring the bedding is perfectly level and flush with the incoming step flights.

- Entrance Staircase Landing: Supply and install heavy-duty natural marble slabs for the main outdoor entrance staircase landing, ensuring a microscopic outward slope to prevent exterior rain puddle formation.

- Entrance Wall Cladding: Supply and install premium natural marble cladding slabs across the walls of the main entrance lobby. Marble panels must be secured using a combination of structural bedding mortar and mechanical stainless-steel anchors or clips to ensure permanent vertical stability.

### External Courtyard Tiling

- Courtyard Floors: Supply and install durable, weather-resistant Egyptian ceramic tiles measuring 40 × 40 cm. Tiles must be bedded on a 1:4 cement mortar layer over a well-compacted sub-base or external concrete apron.

- Slope and Drainage: All courtyard tiling must be precisely sloped toward external storm-water drainage channels or gully traps to ensure efficient surface water runoff during heavy rainfall.

## Execution, Workmanship, and Quality Control

- Substrate Preparation: Before applying mortar, all concrete floors must be thoroughly swept clean of dust, oil, paint drops, or loose plaster. The bare concrete must be lightly wetted with clean water to prevent it from rapidly absorbing the mixing water from the fresh mortar bed.

- Leveling and Alignment Checks: The contractor must use laser levels or nylon line grids across all rooms and corridors. The supervising engineer will inspect the dry tile layout and leveling lines before permanent mortar setting begins.

- Protection of Finished Works: Newly tiled floors must be barred from all foot traffic for a minimum of 24 hours post-installation. Completed flooring must be covered with protective heavy-duty canvas, building paper, or plastic sheets to prevent scratching or chipping during subsequent construction activities.

- Final Cleansing: Upon completion of all grouting and curing phases, all tiled surfaces must be thoroughly washed with clean water and mild, non-acidic detergents to remove film, dust, and stubborn mortar stains, leaving a flawless, ready-for-handover finish.

## Painting

Internal Paint

Acrylic emulsion.

Properties:

- washable;

- anti-fungal;

- low VOC.

Minimum:

- one primer coat;

- two finishing coats.

External Paint

Weather-shield acrylic system:

- UV resistant;

- water resistant;

- anti-carbonation.

Minimum:

- one sealer coat;

- two finish coats.

## Technical Specifications (Painting)

### 6.1.1 Material Standards and Approvals

- Paint Quality: All finishing paints must be first-grade silk paint manufactured by Jotun (e.g., Fenomastic series for interiors, Jota shield series for exteriors) or an approved equivalent premium brand.

- Sample Submission: Before any paint or putty is delivered to the job site, the contractor must apply mock-up samples (minimum 1.0 m × 1.0 m patches) on the walls for color, texture, and gloss approval by the supervising engineer.

### 6.1.2 Interior Walls Painting

- Surface Preparation: Scrap away all loose mortar, dust, and debris. Apply approved high-quality wall putty filler in successive layers. Sand down each layer with fine-grade sandpaper to achieve a perfectly flat, uniform, and plumb surface.

- Application System: Apply one base primer coat followed by three (3) separate coats of premium plastic emulsion silk paint. Each coat must be allowed to dry completely and be lightly sanded before the next coat is applied. The final surface must be free of brush marks, roller stipples, runs, or color variations.

### 6.1.3 Exterior Walls, Stairwells, and Parapet Walls Painting

- Surface Preparation: Level all rough concrete and masonry substrates using a structural sand-cement mortar rendering coat. Fill all minor voids, blowholes, and surface honeycombing to ensure a uniform plane.

- Application System: Apply a specialized exterior alkali-resistant primer coat, followed by three (3) separate coats of premium weatherproof exterior silk paint. The final finish must provide robust UV protection and resistance to environmental weathering.

### 6.1.4  Room and Corridor Ceilings Painting

- Surface Preparation: Clean all ceiling concrete surfaces, remove formwork release oils, and apply a thin layer of specialized ceiling putty or joint compound to eliminate imperfections. Sand smoothly.

- Application System: Apply one primer coat followed by three (3) separate coats of premium plastic emulsion paint, matching the exact surface execution and seamless finish required for the interior walls.

### 6.1.5 Execution, Workmanship, and Quality Control

- Protection of Fixtures: Prior to starting any preparation or painting, the contractor must completely mask and protect all floors, electrical boxes, windows, door frames, and completed plaster works using plastic sheeting and masking tape.

- Drying Time Intermissions: The contractor must strictly adhere to the manufacturer’s data sheets regarding drying times between successive coats. No subsequent coat shall be applied until the supervising engineer inspects and approves the previous layer.

- Environmental Constraints: Do not apply exterior paint during dusty conditions, high winds, rain, or when ambient temperatures exceed the maximum limits specified by Jotun (typically 40°C).

- Final Lighting Inspection: The final finished paintwork will be inspected under cross-lighting conditions. Any visible patches, waves, transparency issues, or uneven gloss must be corrected by the contractor at their own expense.

# Technical Specifications (Epoxy)Material Requirements

- Epoxy Paint System: Must be a high-build, self-leveling, fiber-reinforced epoxy coating system (such as Epoxy Fiber or an approved medical-grade equivalent) designed for heavy foot traffic, chemical resistance, and sterile environments.

- Performance Attributes: The cured system must be completely seamless, non-porous, antibacterial, easy to sanitize, and resistant to medical disinfectants, blood, and laboratory chemicals. It must achieve a minimum compressive strength of 50 N/mm² to withstand medical equipment loads.

  - Substrate and Surface Preparation

- Mechanical Profiling: The underlying concrete slab must be thoroughly clean, structurally sound, and completely dry (moisture content must not exceed 4% when tested with a calcium chloride or digital moisture meter).

- Remediation: Use mechanical floor grinders equipped with dust-extraction vacuums to remove all curing compounds, laitance, old paint, oils, and grease. Blowholes, cracks, and surface pits must be filled flush using an approved solvent-free epoxy putty repair compound.

- Priming: Apply one uniform coat of a high-penetration epoxy primer to seal the concrete pores and ensure maximum chemical bonding between the substrate and the subsequent epoxy coats.

### Epoxy Application and Execution

- First Coat Application: Once the primer has cured to a tack-free state, mix the fiber-reinforced epoxy components strictly according to the manufacturer’s instructions using a low-speed mechanical mixer. Apply the first coat uniformly using a notched squeegee or lint-free roller in a single direction (e.g., East-West).

- Second Coat Application: Allow the first coat to dry within the manufacturer's specified recoat window. Apply the second coat exactly perpendicular to the first coat (e.g., North-South). This cross-directional roll ensures a perfectly level surface, uniform thickness, and eliminates any potential pinholes or tracking marks.

- Final Finish: The completed floor system must cure to a perfectly smooth, level, satin or gloss finish with a total dry film thickness (DFT) that complies with the manufacturer's heavy-duty medical traffic data sheets.

## Execution, Workmanship, and Quality Control

- Dust and Contamination Control: Because these are medical delivery, nursery, and laboratory spaces, the application area must be completely sealed off using plastic sheeting isolation barriers. No dust, insects, or floating airborne particles are permitted in the rooms during the application and curing phases.

- Cove Base Integration (Sanitary Detailing): At the junctions where the floor meets the walls, the epoxy must be turned up the wall to create a seamless, radiused cove skirting (typically 10 cm to 15 cm high) if required by the clinical design, eliminating sharp 90-degree corners where bacteria can accumulate.

- Curing Timeline: The treated rooms must be kept under strict climate control (ideally between 15°C and 30°C) and completely locked down. Light foot traffic is restricted for at least 24 hours, and heavy mechanical equipment or medical furniture installation must not occur until a full 7-day chemical cure is reached.

- Testing and Inspection: The supervising engineer will inspect the final cured floor for levelness, complete opacity, the total absence of air bubbles, blisters, or roller lint, and absolute adhesion to the substrate before handover.

# Division 22 – Water Supply and Plumbing

## PPR Water Piping

The BOQ requires German-manufactured PPR pipe systems.

Acceptable standards:

- DIN 8077

- DIN 8078

Pressure Class:

| Service | Rating |
| --- | --- |
| Cold Water | PN16 |
| Hot Water | PN20 |

## Pipe Installation

Joining method:

- thermal fusion only.

Threaded connections shall not be used except at equipment interfaces.

Pipe supports:

| Pipe Diameter | Maximum Spacing |
| --- | --- |
| 20-25 mm | 1.0 m |
| 32-50 mm | 1.5 m |
| 63 mm+ | 2.0 m |

## Pressure Testing

Hydrostatic test pressure:

- 1.5 times working pressure.

Test duration:

- 2 hours minimum.

Acceptance:

- zero visible leakage;

- pressure loss less than 5%.

## Division 22.4 UPVC Drainage System

Drainage pipes shall be:

- UPVC Schedule 80;

- solvent welded.

Minimum diameters:

| Service | Diameter |
| --- | --- |
| Basin | 50 mm |
| Floor drain | 75 mm |
| WC branch | 110 mm |
| Main sewer | 160 mm |

## Sanitary Fixtures

Western WC

- Vitreous china.

- Dual flush.

- Maximum flush 4.5 liters.

## Squat WC

- Vitreous china.

- Heavy-duty hospital grade.

- Slip-resistant footrests.

## Wash Basins

- Vitreous china.

- Wall mounted.

- Chrome plated mixer.

Working pressure:

- 1-6 bar.

## Division 22.6 Water Storage Tanks

The BOQ includes 2000-liter storage tanks with booster systems.

Tank requirements:

- UV stabilized polyethylene.

- Triple-layer construction.

- Food-grade material.

The tank shall be mounted on:

- galvanized steel support frame.

Design load:

- full water load + 25% safety factor.

## Division 22.7 Booster Pumps

Pump body:

- stainless steel AISI 304.

Impellers:

- stainless steel.

Motor:

- IP55 minimum.

Control panel shall include:

- dry run protection;

- overload protection;

- automatic operation.

## Division 22.8 Septic Tank Construction

The septic tank identified in the BOQ shall be constructed using reinforced concrete.

Internal walls:

- minimum 200 mm thick.

Concrete:

- C25 minimum.

Waterproofing:

- internal cementitious waterproof coating.

## Testing

Before acceptance:

- fill with water;

- retain water for 72 hours.

Permitted leakage:

- none.

## Division 22.9 Soak-Away Pit

The soak-away pit shall:

- be 2 m diameter;

- reach approved depth;

- be lined with masonry or reinforced concrete rings as approved by Engineer.

Surrounding filter media:

- graded crushed stone 25-75 mm.

## Division 23 – HVAC

### Split Air Conditioning Units

Units shall:

- be inverter type;

- operate at ambient temperatures up to 52°C;

- use R32 refrigerant or approved equivalent.

Minimum EER:

- 3.2

### Copper Pipework

Copper tubing:

- ASTM B280.

Insulation:

- closed-cell elastomeric insulation;

- minimum thickness 13 mm.

## Commissioning

Contractor shall perform:

- nitrogen pressure test;

- vacuum test;

- refrigerant charge verification;

- 4-hour operational test.

## Division 26  Electrical Works

### Wiring

Conductors:

- stranded copper;

- PVC/XLPE insulated;

- 600/1000 V rated.

Minimum cable sizes:

| Circuit | Minimum Size |
| --- | --- |
| Lighting | 2.5 mm² |
| Socket outlets | 4 mm² |
| AC circuits | 6 mm² |

### Distribution Boards

Distribution boards shall:

- be powder-coated steel;

- IP54 minimum;

- include lockable doors;

- include circuit schedules.

### Earthing

Earth roads:

- copper-bonded steel;

- length 3 m minimum.

Maximum earth resistance:

- 5 Ohms.

### Testing

The Contractor shall submit certified test reports for:

- Continuity testing.

- Insulation resistance testing.

- Earth resistance testing.

- RCD testing.

- Functional testing.

# Technical Specifications (Electrical Works)

## Distribution Equipment and Switches

- Main Distribution Board (MDB): Supply and install a 24-way metal-clad distribution board. The board must feature factory-fitted copper busbars, neutral bars, and isolated earth bars. It must be equipped with a matching 100 Amp safety switch (main circuit breaker) providing over-current and short-circuit protection.

- Power Sockets: Supply and install premium-grade Tenby brand flush-mounted accessories. This includes 13 Amp switched shuttered socket outlets for general ring/radial power circuits and 16 Amp socket outlets for dedicated heavy-appliance radial circuits.

- A/C Isolators: Supply and install Tenby 45 Amp double-pole (DP) water heater style switches fitted with neon indicators to serve as local isolation switches for all air conditioning units.

## Lighting and Ventilation Systems

- Room and Hallway Lighting: Supply and install 4-foot Philips fluorescent/Neon light fixtures, complete with electronic ballasts, starter mechanisms, high-efficiency tubes, localized switches, and intermediate wiring connections.

- Bathroom Lighting: Supply and install 2-foot English-made fluorescent/Neon ceiling light fixtures. These units must feature vapor-proof or moisture-resistant enclosures suitable for damp bathroom environments.

- Operating Room Lighting: Supply and install high-intensity, specialized flood lights designed specifically for medical operating rooms. These fixtures must provide shadowless, high-color-rendering illumination, and be safely wired to dedicated clean-power circuits.

- Ceiling Fans: Supply and install heavy-duty 56-inch ceiling fans, including down rods, safety hooks, motor assemblies, wiring, and matching multi-step speed wall regulators.

- Wall Fans: Supply and install Orient (Indian make) wall-mounted mechanical fans, complete with swivel-oscillation mechanisms, pull-cord or digital controls, mounting brackets, and local power connections.

- Exhaust Ventilation: Supply and install heavy-duty mechanical exhaust fans for all bathroom and laboratory spaces to ensure proper air changes. Laboratory units must be chemically resistant if specified by the layout.

## Air Conditioning and HVAC Infrastructure

- Window A/C Units: Supply and install O General Window brand (or approved equivalent) Freon air conditioning units in designated wall sleeves. Available in two capacities: 24,000 BTU and 18,000 BTU.

- Split A/C Units: Supply and install O General brand (or approved equivalent) split-type air conditioning units comprising indoor high-wall evaporators and outdoor condensing units. Available in two capacities: 24,000 BTU and 18,000 BTU.

- HVAC Connections and Drainage: All A/C installations must include structural mounting brackets, refrigerant copper piping insulated with elastomeric foam, interlocking control wiring, and a dedicated uPVC condensate drain pipe routed with a continuous downward slope connected to the nearest return water or greywater drainage point.

# Division  – Medical Waste Incinerator

## General

The medical waste incinerator specified in the BOQ shall be suitable for treatment of infectious healthcare waste.

## Combustion Requirements

Primary chamber:

- minimum 800°C.

Secondary chamber:

- minimum 1100°C.

Residence time:

- minimum 2 seconds.

## Refractory Lining

High-alumina refractory brick:

- minimum thickness 114 mm.

Insulating layer:

- minimum 50 mm ceramic insulation.

## Chimney

Material:

- stainless steel.

Height:

- Minimum 6 m above finished ground level.

## Testing

The Contractor shall undertake:

- dry commissioning;

- operational commissioning;

- trial burn test;

- temperature verification.

# Construction of a Medical Waste Incinerator

## Technical Specifications

### Dimensions & Geometric Footprint

- Base Area Footprint: 2500 mm × 2500 mm overall outer dimension at ground level.

- Structural Vertical Height: 2720 mm overall height measured from the natural ground line to the concrete slab roof cap (excluding the vertical extension of the metal chimney).

- Operating Capacities: Designed as a natural-draught dual-chamber configuration with a nominal throughput capacity matching localized clinical demands (~12 to 15 kg/hour).

### Civil & Concrete Substructure Works

- Mass Concrete Foundation: Cast an unreinforced or minimally reinforced structural foundation slab measuring 2500×2500 mm with an overall vertical thickness/depth of 650 mm.

- Concrete Strength Specification: Grade C20/25 nominal mix (1:2:4 ratio by volume) using pure Portland Cement, clean potable water, well-graded coarse aggregates (maximum aggregate size 20 mm), and washed river sand.

- Ash Pit Profile: Integrated directly below the primary combustion chamber, featuring smooth cement mortar rendering along internal faces to facilitate frictionless ash removal using long-handled scrapers.

- Concrete Access Steps: Monolithically cast concrete step structures provided at the designated loading bay face to afford operators an ergonomic, safe platform height during waste charging sequences.

### Masonry & Thermal Barrier Linings

- Primary Combustion Chamber Lining: Inner chamber surfaces exposed directly to active flames must be lined with premium refractory firebricks capable of withstanding continuous operational temperatures exceeding 850°C to 1100°C.

- Refractory Mortar Jointing: All firebricks must be laid exclusively with high-temperature refractory fireclay mortar (composed of premixed calcium-aluminate cement or specialized kaolin clays) with tight joints not exceeding 3 mm thickness.

- Exterior Protective Envelope: The outer structural walls above ground level shall be constructed using high-quality, well-burnt solid local clay bricks (1.5-brick thick layout configuration) laid in a highly workable 1:4 cement-to-sand mortar matrix, meticulously plumbed, joint-struck, and cured.

### Metallurgical, Chimney & Metalwork Assemblies

- Exhaust Chimney Stack: Supply, fabricate, and install a vertical high-clearance exhaust chimney stack mounted securely through the top concrete roof slab.

  - Material: Minimum 4 mm thick heat-resistant mild steel or stainless steel pipe.

  - Diameter: Minimum 150 mm inside diameter (or as detailed on the approved UNOPS reference drawings).

  - Height: The stack must rise to a minimum vertical clearance of 4 to 5 meters above the concrete slab cap to ensure proper natural draught and safe dispersion of emissions.

  - Accessories: The chimney must be topped with an integrated conical rainwater cowl (spark arrestor) and rigidly anchored using high-tensile guy wires or welded structural steel support brackets to withstand local wind loads.

- Combustion Metal Grill (Grate): Fabricated using high-grade, heat-resistant cast iron or solid steel bars (minimum 20 mm diameter), spaced at 50 mm intervals center-to-center to endure intense thermal cycling without warping.

- Loading & Ash Clean-Out Doors: Formed from heavy-gauge, minimum 4 mm thick structural mild steel plates backed by dense ceramic fiber insulation blankets. Both doors must feature counterweighted hinge mechanisms and tight-fitting latches to ensure a complete, airtight secondary chamber seal.

## Execution, Workmanship, and Quality Control

- Refractory Curing Intermission: Following the completion of the firebrick masonry and refractory mortar lining, the structural shell must be allowed to dry naturally for at least 7 to 14 days. The contractor must then execute a controlled, slow-temperature wood-fire preheating phase to drive out residual moisture and cure the mortar bonds before full high-temperature operation.

- Metalwork Thermal Expansion: All internal structural steel supports, metal grills, and door frames must be installed with explicit expansion joints (minimum 10 mm to 15 mm clear gap packed with ceramic fiber rope) to prevent the steel from buckling or cracking the brickwork when expanding at high temperatures.

- Emissions and Draft Verification: The supervising engineer will conduct an initial operational trial run using standard test waste to verify that the mechanical charging doors lock tightly, the chimney stack draws exhaust smoothly without smoke backing out, and the ash pit doors maintain an airtight seal.

- Anti-Corrosion Painting: All external, non-insulated structural steel elements, door hinges, latch mechanisms, and the chimney stack base must be cleaned of mill scale and finished with two coats of high-temperature silicone-based aluminum paint capable of resisting temperatures up to 600°C.

11. PSA Medical Oxygen Generation Plant

11.1  General

The Contractor shall supply, deliver, install, test, commission, and hand over a complete turnkey Pressure Swing Adsorption (PSA) Medical Oxygen Generation Plant for onsite production and cylinder filling of medical oxygen. The plant shall be designed, manufactured, and installed as a complete integrated system capable of safe, reliable, and continuous operation under local environmental conditions.

All equipment shall be new, unused, of current manufacture, and suitable for medical oxygen service. The Contractor shall provide all equipment, materials, accessories, controls, piping, electrical systems, safety devices, training, spare parts, documentation, and ancillary works necessary for a fully operational facility.

The oxygen generation plant shall comply with ISO 80601-2-69 and all applicable international standards governing medical oxygen generation systems, pressure vessels, electrical installations, and occupational safety.

11.2 Operating Conditions

The plant shall be designed to operate continuously under the following site conditions:

- Ambient temperature: Up to +55°C.

- Outdoor dusty environment.

- Continuous operation: 24 hours per day, 7 days per week.

- Installation within the designated oxygen plant building.

- Relative humidity and environmental conditions prevailing at the project location.

The Contractor shall ensure that all supplied equipment is adequately protected against high temperatures, dust ingress, corrosion, and adverse environmental conditions.

11.3 Minimum Performance Requirements

The oxygen generation system shall achieve the following minimum performance criteria:

- Oxygen production capacity: Minimum 40 Nm³/hr.

- Oxygen purity: 93% ±3%.

- Cylinder filling capacity: Minimum 50 to 70 cylinders per day.

- Cylinder filling pressure: 150-200 bar.

- Continuous operation without loss of performance under specified ambient conditions.

- Fully automatic operation through PLC-based controls.

The Contractor shall guarantee the specified oxygen production and purity levels during commissioning and acceptance testing.

11.4 Scope of Supply

The supply shall include, but not be limited to, the following major equipment:

11.4.1 Air Compression System

- Oil-free or medical-grade air compressor system suitable for oxygen production applications.

- Air intake filters.

- Air receiver tank(s).

- Automatic condensate drains.

- Vibration isolators.

- Interconnecting piping and accessories.

The compressor package shall be adequately sized to support the full design capacity of the oxygen generation plant.

11.4.2 Air Treatment System

The air treatment package shall include:

- Refrigerated or adsorption air dryer.

- Pre-filters.

- Coalescing filters.

- Activated carbon filters where required.

- After-filters.

- Automatic drainage arrangements.

The air treatment system shall deliver compressed air of suitable quality for PSA oxygen production and shall be designed to minimize moisture, particulates, and oil carryover.

11.4.3 PSA Oxygen Generator

The PSA oxygen generator shall include:

- Twin adsorption vessel arrangement.

- Molecular sieve beds.

- Automatic switching valves.

- Oxygen collection manifold.

- Oxygen storage receiver.

- Control instruments and transmitters.

- Structural frame and supports.

The generator shall be capable of maintaining the specified oxygen purity throughout its operating range.

11.4.4 Oxygen Storage and Filling System

The oxygen storage and cylinder filling system shall include:

- Oxygen receiver tank(s).

- Oxygen booster compressor.

- High-pressure piping and fittings.

- Cylinder filling manifold.

- Flexible filling hoses.

- Pressure gauges.

- Isolation valves.

- Safety relief valves.

The filling system shall permit safe and efficient filling of cylinders to pressures between 150 and 200 bar.

11.5 Instrumentation and Control System

The plant shall be equipped with an automatic PLC-based control system with Human Machine Interface (HMI).

The control system shall provide:

- Automatic operation.

- Start-up and shutdown sequencing.

- Oxygen purity monitoring.

- Pressure monitoring.

- Compressor control.

- Alarm management.

- Fault diagnostics.

- Event logging.

- Emergency shutdown functionality.

The HMI shall provide operators with real-time system status and operational data.

11.6 Oxygen Monitoring System

The plant shall be equipped with a continuous oxygen analyzer capable of monitoring oxygen purity.

The analyzer shall:

- Display oxygen purity continuously.

- Activate alarms if oxygen purity falls outside acceptable limits.

- Interface with the main control system.

- Be suitable for continuous industrial operation.

11.7 Electrical Works

The Contractor shall undertake a complete assessment of electrical requirements and provide a complete electrical installation for the oxygen plant.

Electrical works shall include:

- Load calculations.

- Main Distribution Board (MDB) dedicated to the oxygen plant.

- Motor Control Panel (MCP).

- Circuit breakers and protection devices.

- Motor starters.

- Power cabling.

- Control wiring.

- Equipment interconnections.

- Earthing and bonding systems.

- Surge protection devices.

- Testing and commissioning.

All electrical equipment shall be sized for the connected load and starting currents of the installed equipment.

Electrical installations shall comply with applicable national electrical regulations and recognized international standards.

11.8 Safety Requirements

The oxygen plant shall incorporate all necessary safety provisions including:

- Emergency shutdown system.

- High and low pressure alarms.

- High temperature alarms.

- Oxygen purity alarms.

- Safety relief valves.

- Fire extinguishers suitable for oxygen-enriched environments.

- Warning notices and safety signage.

- Isolation facilities.

- Lock-out/tag-out provisions.

All oxygen service components shall be cleaned for oxygen service and supplied free of oil, grease, and other combustible contaminants.

11.9 Fire Protection

The Contractor shall provide fire protection measures suitable for an oxygen generation and cylinder filling facility, including:

- Portable fire extinguishers.

- Safety signage.

- Emergency response instructions.

- Fire safety equipment required by applicable regulations.

- Personnel safety measures around oxygen storage and filling areas.

11.10 Building Integration Requirements

The Contractor shall coordinate with the building works and ensure that:

- Equipment layout permits safe operation and maintenance access.

- Adequate ventilation is provided.

- Equipment is protected from direct sunlight.

- Dust ingress is minimized.

- Foundations and supports comply with equipment requirements.

- Safe access is provided for cylinder handling and maintenance activities.

11.11 Environmental, Health, Safety and Social (EHSS) Requirements

The Contractor shall comply with all project EHSS requirements and shall:

- Prepare and implement site-specific risk assessments.

- Provide all required Personal Protective Equipment (PPE).

- Ensure safe handling of high-pressure systems.

- Prevent environmental pollution.

- Properly manage wastes and packaging materials.

- Maintain safe work practices throughout implementation.

- Comply with all applicable labor, health, safety, and environmental regulations.

12. Submittals

Prior to procurement and installation, the Contractor shall submit the following for review and approval:

- Detailed shop drawings.

- General arrangement drawings.

- Process flow diagrams.

- Piping and Instrumentation Diagrams (P&ID).

- Electrical single-line diagrams.

- Equipment data sheets.

- Manufacturer catalogues.

- Foundation requirements.

- Equipment layouts.

- Quality control documentation.

- Factory test certificates.

13. Testing and Commissioning

The Contractor shall carry out comprehensive testing and commissioning including:

- Factory acceptance testing where applicable.

- Installation inspection.

- Electrical testing.

- Functional testing.

- Instrument calibration.

- Oxygen purity verification.

- Capacity testing.

- Cylinder filling tests.

- Safety system verification.

- Continuous operation test.

The plant shall demonstrate achievement of all specified performance requirements before acceptance.

14. Training

The Contractor shall provide comprehensive operation and maintenance training for a minimum of ten (10) Employer personnel.

Training shall include:

- Plant operation.

- Routine inspections.

- Preventive maintenance.

- Troubleshooting procedures.

- Safety requirements.

- Emergency procedures.

- Record keeping and reporting.

15. Spare Parts

The Contractor shall provide a complete set of recommended operational and maintenance spare parts sufficient for a minimum of six (6) months of normal operation.

A detailed spare parts list shall be submitted with part numbers, descriptions, and recommended stock quantities.

16. Documentation

Upon completion, the Contractor shall submit:

- As-built drawings.

- O&M manuals.

- Equipment data sheets.

- Spare parts catalogue.

- Calibration certificates.

- Factory test reports.

- Site testing and commissioning reports.

- Warranty certificates.

- Training records.

Documentation shall be provided in both hard-copy and electronic format.

17. Warranty and Defects Liability

The oxygen plant and all associated equipment shall be covered by a minimum twenty-four (24) month manufacturer's warranty from the date of commissioning and acceptance.

The Contractor shall provide a minimum twelve (12) month Defects Liability Period (DLP) following commissioning and handover. All defects, failures, deficiencies, and non-conformities identified during this period shall be rectified by the Contractor at no additional cost to the Employer.

18. Basis of Measurement

The item shall be measured as a complete turnkey PSA Medical Oxygen Generation Plant including all equipment, installation, testing, commissioning, training, spare parts, electrical works, safety systems, documentation, warranties, and all incidental works necessary for a fully operational facility. No separate payment shall be made for components or activities required to achieve a complete and functioning system.

# Appendix X: Handover Documentation and Final Deliverables

Upon completion of all rehabilitation works, the Contractor shall submit a complete set of handover documentation to the Engineer and the Employer. The submission shall demonstrate that all works have been executed, tested, commissioned, and completed in accordance with the Contract Documents, approved drawings, technical specifications, applicable standards, and the Engineer's instructions.

The Contractor shall be responsible for compiling, organizing, and submitting all required records and documents in both hard-copy and electronic formats. All documents shall be provided in clear, legible, and professionally organized form.

## X1. As-Built Documentation

The Contractor shall prepare and submit comprehensive As-Built Drawings reflecting the actual works constructed on site. The drawings shall include, but not be limited to:

- Architectural layouts and modifications.

- Structural rehabilitation and repair works.

- Water supply systems and pipe networks.

- Sanitary and drainage systems.

- Septic tanks, manholes, inspection chambers, and related infrastructure.

- Electrical installations and distribution systems.

- HVAC systems, where applicable.

- Medical waste management facilities and incinerator installations, where applicable.

- External works and site infrastructure.

As-built drawings shall clearly indicate all deviations from the original design and shall be certified by the Contractor prior to submission.

## X2. Testing and Commissioning Records

The Contractor shall submit complete testing and commissioning records for all installed and rehabilitated systems, including:

- Water supply network testing reports.

- Plumbing pressure testing reports.

- Drainage and sanitary system testing reports.

- Septic tank water-tightness testing reports.

- Electrical testing and commissioning reports.

- Earthing and electrical protection test certificates.

- Lighting performance and functional testing reports.

- HVAC commissioning records.

- Equipment start-up and operational testing reports.

- Medical waste incinerator commissioning and operational verification reports, where applicable.

All reports shall be signed by qualified personnel and approved by the Engineer.

## X.3 Quality Assurance and Quality Control Records

The Contractor shall submit all quality documentation generated during project implementation, including:

- Material approval records.

- Factory certificates and manufacturer's compliance certificates.

- Laboratory test reports.

- Inspection and approval records.

- Non-conformance reports and corrective actions undertaken.

- Quality checklists.

## X.4 Operation and Maintenance Manuals

The Contractor shall provide complete Operation and Maintenance (O&M) Manuals for all installed equipment, systems, and facilities.

The manuals shall include:

- Description of equipment.

- Manufacturer's data sheets.

- Operating procedures.

- Preventive maintenance requirements.

- Recommended maintenance schedules.

- Troubleshooting procedures.

- Spare parts lists.

- Safety precautions.

- Warranty information.

- Supplier and manufacturer contact details.

Manuals shall be provided in English and, where requested by the Employer, key operational instructions shall also be provided in Arabic.

## X.5 Training Requirements

Prior to final handover, the Contractor shall provide adequate training to hospital personnel designated by the Employer.

Training shall cover:

- Operation of water supply systems.

- Operation of electrical systems and distribution boards.

- Operation and maintenance of pumps and storage facilities.

- Use and maintenance of HVAC systems.

- Operation of medical waste incinerators and waste management facilities.

- Routine maintenance requirements for rehabilitated infrastructure.

Training records, attendance sheets, and training materials shall be submitted as part of the handover documentation.

## X.6 Warranties and Guarantees

The Contractor shall submit all warranties, guarantees, and manufacturer certifications associated with the completed works and supplied equipment.

These shall include:

- Equipment manufacturer's warranties.

- Waterproofing system warranties.

- Electrical installation warranties.

- Pump and mechanical equipment warranties.

- HVAC equipment warranties.

- Specialized system warranties required under the Contract.

Warranty periods shall commence from the date of Taking-Over Certificate issuance unless otherwise specified in the Contract.