SCOPE OF WORK (SOW) & TECHNICAL SPECIFICATIONS 
Location: Aldamer Teaching Hospital, River Nile State

SISSIRP – Rehabilitation and Upgrading of Aldamer Teaching Hospital

Contents

SECTION I: SCOPE OF WORK	2

1. Introduction	2

2. General Requirements	4

2.2 Verification of Existing Conditions	5

2.3 Hospital Operations and Infection Prevention and Control	5

2.4 Health, Safety and Environmental Management	5

3. Demolition and Removal Works	6

4. Civil and Structural Rehabilitation Works	6

4.1 Concrete Works	6

4.2 Masonry Works	6

4.3 Structural Repairs and Rehabilitation	7

5. Roofing and Waterproofing Works	7

5.2 Waterproofing Works	7

5.3 Roof Drainage and Protection Measures	7

6. Ceiling Works	7

7. Architectural Finishes	8

7.1 Plaster and Surface Preparation Works	8

7.2 Floor Finishes	8

7.3 Wall Finishes	8

7.4 Painting Works	8

8. Doors, Windows and Metal Works	8

8.1 Doors	9

8.2 Windows	9

8.3 Gates and Metal Works	9

9. Water Supply and Plumbing Works	9

9.1 Water Distribution Network	9

9.2 Water Storage Systems	9

9.3 Plumbing Fixtures and Accessories	10

10. Sanitary Sewerage and Drainage Works	10

10.1 Sanitary Sewer Network	10

10.3 Septic Tanks	10

10.4 Soakaway Pits	10

10.5 Sewage Disposal and Drainage Improvements	11

11. Electrical Works	11

11.1 Power Distribution System	11

11.2 Lighting Systems	11

11.3 Small Power Installations	11

11.4 Electrical Rehabilitation and Connections	11

12. HVAC and Ventilation Works	11

12.1 Air Conditioning Systems	11

12.2 Mechanical Ventilation Systems	12

12.3 Testing and Commissioning	12

13. Hospital Departments Rehabilitation Works	12

13.1 Emergency Department	12

13.2 Waiting Areas	12

13.3 Outpatient Clinics	12

13.4 Male and Female Wards	12

13.5 Pediatric Department	12

13.6 Maternity Department	12

13.7 Intensive Care Unit (ICU)	13

13.8 High Dependency Unit (HDU)	13

13.10 Pharmacy Department	13

13.11 X-Ray Department	13

14. Medical Waste Management Facilities	13

15. External Works	13

15.1 Emergency Gate and Access Improvements	14

15.2 Prefabricated Office Units	14

15.3 External Utilities Rehabilitation	14

15.4 Site Rehabilitation and Restoration	14

16. Testing, Commissioning and Training	14

17. Handover Requirements	14

SECTION II: PROJECT TECHNICAL SPECIFICATIONS	15

Division 03: Concrete Works	16

General	16

Materials	16

Aggregates	17

Reinforcement	17

Concrete Strength	17

Testing	17

Execution, Workmanship, and Quality Control	18

Hot-Weather Concreting	18

General Requirements	18

Temperature Controls & Materials	19

Execution & Placement	19

Curing and Protection	19

Division 07 –Waterproofing and Roof Protection	20

2.1 Roof Slope Screed	20

2.2 Acrylic Waterproofing System	20

2.3 Flood Testing	21

Division 08 – Doors, Windows and Metal Works	21

3.1 Steel Doors	21

3.2 Finishing	21

3.3 Aluminum Windows	22

3.4	Technical Specifications	22

3.5	Pre-Installation Iron Framing	22

3.6	Passageways, Operation Rooms, and Bathrooms, Doors & Windows	22

3.7	Aluminum Skylight Assemblies	23

3.8	Ward Partitions	23

3.9	Execution, Workmanship, and Quality Control	23

3.10	Technical Specifications (Metal Works)	24

3.13	Execution & Finishing Workmanship	26

4. Plastering Technical Specifications	26

4.1	Material Requirements	26

4.2	Exterior Plastering (2 cm Thick)	27

4.3	Structural Crack Remediation Method	27

4.4	Execution, Workmanship, and Quality Control	28

Division 09 – Finishes	28

5.1	Ceramic Wall Tiles	28

5.2	Porcelain Floor Tiles	29

5.3	Tile Testing	29

5.4	Technical Specifications (Tiling Works)	30

5.4.1	General Workmanship and Material Cutting	30

5.4.2	Porcelain Tiling (Rooms and Corridors)	30

5.4.3	Bathroom Ceramic Tiling	30

5.4.4	Natural Marble Works (Staircases and Entrances)	31

5.4.5	External Courtyard Tiling	31

5.5	Execution, Workmanship, and Quality Control	32

Painting	32

1.1	Technical Specifications (Painting)	33

6.1.1 Material Standards and Approvals	33

6.1.2 Interior Walls Painting	34

6.1.3 Exterior Walls, Stairwells, and Parapet Walls Painting	34

6.1.4  Room and Corridor Ceilings Painting	34

6.1.5 Execution, Workmanship, and Quality Control	35

Technical Specifications (Epoxy)Material Requirements	35

7.2	Epoxy Application and Execution	36

7.3	Execution, Workmanship, and Quality Control	36

Division 22 – Water Supply and Plumbing	37

7.4	PPR Water Piping	37

7.5	Pipe Installation	38

7.6	Pressure Testing	38

7.7	Division 22.4 UPVC Drainage System	39

7.8	Sanitary Fixtures	39

7.9	Squat WC	39

7.10	Wash Basins	39

7.11	Division 22.6 Water Storage Tanks	40

7.12	Division 22.7 Booster Pumps	40

7.13	Division 22.8 Septic Tank Construction	40

7.14	Testing	41

7.15	Division 22.9 Soak-Away Pit	41

Division 23 – HVAC	41

7.15.1	Split Air Conditioning Units	41

7.15.2	Copper Pipework	42

7.16	Commissioning	42

Division  Electrical Works	42

7.16.1	Wiring	42

7.16.2	Distribution Boards	43

7.16.3	Earthing	43

7.16.4	Testing	43

7.17	Technical Specifications (Electrical Works)	43

7.18	Distribution Equipment and Switches	44

7.19	Lighting and Ventilation Systems	44

7.20	Air Conditioning and HVAC Infrastructure	45

Division  – Medical Waste Incinerator	45

7.21	General	45

7.22	Combustion Requirements	45

7.23	Refractory Lining	46

7.24	Chimney	46

7.25	Testing	46

7.26	Construction of a Medical Waste Incinerator	46

7.27	Technical Specifications	46

7.27.1	Dimensions & Geometric Footprint	46

7.27.2	Civil & Concrete Substructure Works	47

7.27.3	Masonry & Thermal Barrier Linings	47

7.27.4	Metallurgical, Chimney & Metalwork Assemblies	48

7.28	Execution, Workmanship, and Quality Control	48

Appendix X: Handover Documentation and Final Deliverables	49

As-Built Documentation	50

Testing and Commissioning Records	50

11.3 Quality Assurance and Quality Control Records	51

11.4 Operation and Maintenance Manuals	51

11.5 Training Requirements	52

11.6 Warranties and Guarantees	52

# SECTION I: SCOPE OF WORK

## 1. Introduction

The Works comprise the rehabilitation, upgrading, and improvement of Aldamer Teaching Hospital in River Nile State with the objective of restoring and enhancing the hospital's operational functionality, safety, efficiency, and healthcare service delivery capacity. The project includes all architectural, structural, mechanical, electrical, plumbing, drainage, sanitation, medical waste management, and associated external works required to rehabilitate the designated hospital facilities and support infrastructure in accordance with the Contract Documents, Bills of Quantities, approved drawings, approved submittals, and the SISSIRP Unified Technical Specifications.

The Contractor shall provide all labor, materials, equipment, tools, transportation, supervision, temporary facilities, utilities, testing services, commissioning activities, documentation, and all other resources necessary for the complete execution and handover of the Works. The Contractor shall execute the Works in a manner that minimizes disruption to ongoing healthcare services and ensures the continuous operation of the hospital throughout the construction period, while maintaining a safe environment for patients, visitors, and hospital staff.

The rehabilitation works are primarily focused on the Emergency and Trauma Department and its associated facilities, including the reconfiguration and upgrading of the existing clinical layout to improve patient flow and emergency response functions. The scope includes the construction of three additional administrative offices, replacement of the main entrance gate, establishment of dedicated Trauma and Resuscitation Rooms, expansion of the Pediatric Ward to provide short-stay observation facilities, and rehabilitation and replacement of the existing water supply and sewerage systems to address leakage and drainage issues affecting the basement level.

The project further includes the complete rehabilitation and upgrading of the General Intensive Care Unit (ICU), including patient treatment areas, sanitary facilities, staff support and rest areas, internal finishes, building services, and all related infrastructure required to ensure compliance with current healthcare operational requirements. In addition, the Works include rehabilitation of the General Intermediate Care Ward and the High Dependency Unit (HDU) within the Obstetrics and Gynecology Ward, including all associated architectural, mechanical, electrical, plumbing, medical, and support service installations necessary to restore their full operational functionality.

The scope also includes the construction, installation, testing, and commissioning of a new Medical Waste Incinerator together with all associated infrastructure, utility connections, safety measures, and environmental protection requirements necessary for the safe management and disposal of healthcare waste. Furthermore, site improvement works shall be undertaken, including backfilling, grading, drainage improvements, and rehabilitation of the external area located in front of the hospital cafeteria, together with other ancillary external works required to improve accessibility, safety, and the overall functionality of the hospital premises.

Prior to commencing any construction activities, the Contractor shall prepare and submit detailed Method Statements, Shop Drawings, Material Submittals, Product Data Sheets, Samples where applicable, and all other technical submissions required for the execution of the Works. All submissions shall be reviewed and approved by the Engineer/Consultant before implementation. No portion of the Works shall proceed without the necessary approvals, and the Contractor shall ensure full coordination between all disciplines and compliance with the Contract Documents, Technical Specifications, site conditions, and hospital operational requirements. Any work executed without the required approvals shall be subject to rejection and replacement at the Contractor's own cost.

The scope shall further include all temporary works, protection measures, testing, commissioning, training, documentation, as-built drawings, corrective works, and all ancillary activities necessary for the complete and satisfactory delivery of fully functional healthcare facilities ready for safe operation and occupancy

.

## 2. General Requirements

2.1 Mobilization and Site Establishment

The Contractor shall mobilize all personnel, equipment, materials, temporary facilities, and resources required for execution of the Works.

The Contractor shall establish site offices, storage areas, temporary utilities, worker welfare facilities, safety systems, security arrangements, temporary fencing, warning signage, and project information signboards.

The Contractor shall install and maintain project signboards and internal directional signage as detailed in the BOQ.

The Contractor shall engage a qualified Civil Engineer and (other specialties to be added as needed) to supervise and oversee the execution of the relevant works throughout the project implementation

### 2.2 Verification of Existing Conditions

Prior to commencement of any work, the Contractor shall undertake a comprehensive site inspection and verification of existing conditions.

The Contractor shall verify dimensions, levels, utility routes, existing installations, structural conditions, serviceability of systems, and any constraints affecting execution of the Works.

No claim arising from failure to inspect or verify site conditions shall be accepted.

### 2.3 Hospital Operations and Infection Prevention and Control

The Contractor shall develop and implement a phased construction methodology that permits continued operation of hospital services.

Construction activities shall be coordinated with hospital management to avoid disruption of critical functions.

The Contractor shall provide dust barriers, temporary partitions, protective enclosures, and controlled access arrangements around work zones.

All works shall be executed in accordance with Infection Prevention and Control (IPC) requirements applicable to healthcare facilities.

Special attention shall be given to ICU, HDU, maternity wards, laboratory, pediatric, emergency, and X-ray areas.

### 2.4 Health, Safety and Environmental Management

The Contractor shall prepare and implement a Site-Specific Health, Safety, and Environmental Management Plan.

The Plan shall include:

- Risk assessments.

- Emergency procedures.

- Fire prevention measures.

- Safe work procedures.

- Traffic management.

- Waste management.

- Environmental protection measures.

- Personal protective equipment requirements.

- Incident reporting procedures.

The Contractor shall protect hospital staff, patients, visitors, medical equipment, and existing facilities throughout the duration of the Works.

## 3. Demolition and Removal Works

The Contractor shall perform all demolition, dismantling, removal, disposal, and site-clearing works required to facilitate the rehabilitation activities.

The Works shall include removal of damaged finishes, defective building components, deteriorated plumbing fixtures, damaged electrical accessories, abandoned services, unsuitable materials, debris, and any obstructions to the execution of the rehabilitation works.

All demolished materials and construction waste shall be removed from site and disposed of at approved disposal locations.

Reusable materials designated by the Employer shall be carefully removed, protected, and handed over.

## 4. Civil and Structural Rehabilitation Works

### 4.1 Concrete Works

The Contractor shall execute all reinforced concrete works required under the Contract.

The works shall include excavation, formwork, reinforcement, casting, curing, repair, rehabilitation, and reinstatement of concrete elements identified within the BOQ.

Where required, damaged structural elements shall be repaired or reconstructed to restore structural integrity.

### 4.2 Masonry Works

The Contractor shall repair, construct, rebuild, modify, and reinstate masonry walls, partitions, and associated elements affected by the rehabilitation works.

The Works shall include blockwork, mortar works, wall patching, crack repairs, openings, and integration with existing structures.

### 4.3 Structural Repairs and Rehabilitation

The Contractor shall undertake all necessary localized structural repairs identified during implementation and approved by the Engineer.

All structural rehabilitation works shall restore the intended performance, stability, and durability of the affected components.

## 5. Roofing and Waterproofing Works

5.1 Roofing Works

The Contractor shall rehabilitate damaged roof systems and associated roof elements identified in the BOQ.

Works shall include surface preparation, repairs, rehabilitation of roof structures, restoration of roof coverings, and all associated ancillary works.

### 5.2 Waterproofing Works

The Contractor shall provide waterproofing systems including APP membrane waterproofing for roof areas, washrooms, service areas, and all locations specified in the BOQ.

Works shall include substrate preparation, membrane installation, terminations, flashing integration, protection layers, and watertightness testing.

### 5.3 Roof Drainage and Protection Measures

The Contractor shall inspect, repair, and improve roof drainage arrangements to ensure proper runoff and protection against water infiltration.

All drainage outlets, flashing details, and waterproofing interfaces shall be fully functional upon completion.

## 6. Ceiling Works

The Contractor shall repair, replace, rehabilitate, and install ceilings where indicated.

The works shall include suspension systems, ceiling panels, access hatches, finishes, trimming, and coordination with electrical and HVAC installations.

The emergency waiting area ceiling rehabilitation and associated ceiling works identified in the BOQ shall be completed in full.

## 7. Architectural Finishes

### 7.1 Plaster and Surface Preparation Works

The Contractor shall repair damaged plaster, patch defective surfaces, prepare substrates, and restore wall and ceiling surfaces prior to application of finishes.

### 7.2 Floor Finishes

The Contractor shall supply and install mosaic flooring, porcelain floor tiles, floor screeds, floor repairs, grouting, skirting, thresholds, and all related accessories specified in the BOQ.

Finished floor surfaces shall be level, durable, and suitable for healthcare environments.

### 7.3 Wall Finishes

The Contractor shall install wall tiles, repair damaged finishes, execute textured finishes, and apply all wall finish systems included in the BOQ.

### 7.4 Painting Works

The Contractor shall complete all interior and exterior painting works including surface preparation, priming, undercoats, finishing coats, and touch-up works.

Painting works shall be undertaken in wards, clinics, waiting areas, laboratories, maternity units, pediatric wards, ICU, HDU, pharmacy, X-ray department, offices, and all associated facilities identified in the BOQ.

## 8. Doors, Windows and Metal Works

### 8.1 Doors

The Contractor shall supply, install, replace, repair, and adjust new and existing doors specified in the BOQ.

The Works shall include steel doors, aluminum doors, MDF doors, frames, hinges, handles, locks, stoppers, ironmongery, and all accessories necessary for complete installation.

### 8.2 Windows

The Contractor shall supply and install aluminum windows and rehabilitate existing window assemblies where indicated.

All windows shall be complete with hardware, glazing, seals, anchorage systems, and finishing works.

### 8.3 Gates and Metal Works

The Contractor shall fabricate and install the new emergency gate and all associated metal works.

The Contractor shall provide corrosion protection, finishing systems, accessories, locking arrangements, and support structures.

## 9. Water Supply and Plumbing Works

### 9.1 Water Distribution Network

The Contractor shall rehabilitate and extend the hospital water supply system.

The works shall include installation of approximately 300 linear meters of PPR piping and all associated fittings, valves, supports, connections, and accessories.

The Contractor shall ensure uninterrupted supply of water to occupied hospital areas throughout implementation.

### 9.2 Water Storage Systems

The Contractor shall supply and install water storage tanks including four 1,000-liter plastic tanks complete with support structures, fittings, connections, overflows, drains, and control valves.

### 9.3 Plumbing Fixtures and Accessories

The Contractor shall supply, install, replace, and commission sanitary fixtures and plumbing accessories including wash basins, faucets, toilet fixtures, and associated installations specified in the BOQ.

All installations shall be leak-free, fully operational, and connected to functioning water supply and drainage systems.

## 10. Sanitary Sewerage and Drainage Works

### 10.1 Sanitary Sewer Network

The Contractor shall install and rehabilitate approximately 200 linear meters of UPVC sewer network and associated branch connections.

The entire system shall be tested for watertightness and functionality prior to commissioning.

10.2 Manholes and Inspection Chambers

The Contractor shall clean, repair, rehabilitate, and restore all manholes and inspection chambers identified in the BOQ.

Damaged covers, benching, channels, and chamber components shall be repaired or replaced.

### 10.3 Septic Tanks

The Contractor shall construct two new septic tanks complete with reinforced concrete walls, slabs, ventilation systems, pipe connections, access covers, testing, and commissioning.

### 10.4 Soakaway Pits

The Contractor shall construct two new soakaway pits, including excavation, lining, concrete covers, connection pipework, and associated drainage works.

### 10.5 Sewage Disposal and Drainage Improvements

The Contractor shall rehabilitate the existing wastewater disposal systems and sewage wells to ensure proper disposal and environmental compliance.

## 11. Electrical Works

### 11.1 Power Distribution System

The Contractor shall inspect, rehabilitate, modify, and upgrade electrical distribution systems serving the rehabilitated departments.

Works shall include wiring, terminating, reconnection, protection devices, distribution boards, accessories, and associated electrical infrastructure.

### 11.2 Lighting Systems

The Contractor shall supply and install LED light fittings, downlights, spotlights, and associated control devices included in the BOQ.

All lighting systems shall be tested and commissioned.

### 11.3 Small Power Installations

The Contractor shall install sockets, switches, outlets, and accessories required for the rehabilitated hospital departments.

### 11.4 Electrical Rehabilitation and Connections

The Contractor shall carry out testing, repair, reinstatement, and commissioning of all existing electrical systems affected by the rehabilitation works.

## 12. HVAC and Ventilation Works

### 12.1 Air Conditioning Systems

The Contractor shall supply, install, service, test, and commission split air-conditioning units of capacities identified in the BOQ.

The works include installation of new units, replacement of defective units, servicing of existing systems, and provision of all refrigerant piping, controls, insulation, drains, and accessories.

### 12.2 Mechanical Ventilation Systems

The Contractor shall supply and install exhaust fans and ventilation systems required for ICU, HDU, sanitary facilities, and associated hospital spaces.

### 12.3 Testing and Commissioning

All HVAC systems shall be inspected, tested, balanced, commissioned, and demonstrated to operate satisfactorily under design conditions.

## 13. Hospital Departments Rehabilitation Works

### 13.1 Emergency Department

The Contractor shall rehabilitate emergency treatment areas, support spaces, finishes, electrical systems, plumbing systems, HVAC systems, and associated infrastructure.

### 13.2 Waiting Areas

Works shall include wall finishes, texture finishes, ceilings, electrical works, lighting systems, and associated rehabilitation measures.

### 13.3 Outpatient Clinics

The Contractor shall rehabilitate clinic rooms including architectural finishes, sanitary facilities, electrical systems, and environmental control systems.

### 13.4 Male and Female Wards

The rehabilitation shall include flooring, painting, ceilings, plumbing fixtures, electrical systems, ventilation systems, and associated healthcare facility upgrades.

### 13.5 Pediatric Department

The Contractor shall execute all rehabilitation works necessary to restore functionality and improve service delivery within pediatric facilities.

### 13.6 Maternity Department

The Contractor shall rehabilitate maternity spaces and associated support facilities, including architectural finishes and building services.

### 13.7 Intensive Care Unit (ICU)

The work shall include rehabilitation of sanitary facilities, installation of air-conditioning units, exhaust ventilation systems, electrical systems, ceilings, finishes, and associated support works.

### 13.8 High Dependency Unit (HDU)

The Contractor shall rehabilitate HDU facilities including sanitary services, HVAC systems, electrical works, and architectural finishes.

13.9 Laboratory Department

The Contractor shall rehabilitate laboratory spaces, finishes, wash basins, plumbing systems, electrical systems, and associated support infrastructure.

### 13.10 Pharmacy Department

The Contractor shall rehabilitate pharmacy facilities including finishes, electrical systems, storage support infrastructure, and environmental control measures.

### 13.11 X-Ray Department

The Contractor shall rehabilitate the X-Ray Department, including architectural finishes, electrical systems, HVAC services, and associated support works.

## 14. Medical Waste Management Facilities

The Contractor shall construct, install, test, commission, and hand over a medical waste incinerator facility in accordance with the BOQ and applicable Ministry of Health and WHO requirements.

The work shall include all civil works, foundations, utility connections, structural support works, combustion units, access arrangements, protective systems, and associated infrastructure required for fully functional operation.

## 15. External Works

### 15.1 Emergency Gate and Access Improvements

The Contractor shall construct and install the emergency gate and execute all associated access improvements required under the Contract.

### 15.2 Prefabricated Office Units

The Contractor shall supply, install, and commission prefabricated office units complete with doors, windows, electrical systems, air-conditioning provisions, finishes, and associated services.

### 15.3 External Utilities Rehabilitation

The Contractor shall rehabilitate and reroute external water and sewer infrastructure and restore all disturbed utility corridors.

### 15.4 Site Rehabilitation and Restoration

The Contractor shall execute site clearing, backfilling, grading, surface restoration, cleaning, and reinstatement works required to return all disturbed areas to serviceable condition.

All debris generated during the Works shall be removed from site.

## 16. Testing, Commissioning and Training

The Contractor shall undertake all required inspections, testing, commissioning, demonstrations, operational verification, and performance testing for all completed works.

The Contractor shall provide training to designated hospital staff covering operation, maintenance, safety procedures, and routine inspection requirements of all installed systems and equipment.

## 17. Handover Requirements

Upon completion of the Works, the Contractor shall submit the following:

- As-built drawings.

- Testing and commissioning records.

- Quality assurance and quality control documentation.

- Operation and maintenance manuals.

- Equipment schedules and asset registers.

- Warranty certificates and guarantees.

- Manufacturer certificates.

- Training records.

- Defects correction commitments.

The Contractor shall rectify all defects identified during inspections and commissioning activities prior to final acceptance.

The Works shall only be considered complete after successful testing and commissioning, submission of all required documentation, correction of all defects, completion of training requirements, and issuance of the Taking-Over Certificate by the Employer.

# SECTION II: PROJECT TECHNICAL SPECIFICATIONS

To Be Read Together with the SISSIRP Unified Technical Specifications.

"To be read in conjunction with the SISSIRP Unified Technical Specifications. In case of discrepancies between the unified specifications and item-specific descriptions, the provisions of this document shall prevail, subject to the approval of the IOM Engineer."

## Division 03: Concrete Works

### General

Concrete works shall include all reinforced concrete elements required under the rehabilitation works, including:

- Roof screeds.

- Water tank supports.

- Pump foundations.

- Manholes.

- Septic tank structures.

- Soak-away structures.

- Access slabs.

- Stair repairs.

- Structural rehabilitation works.

### Materials

#### Cement

- Ordinary Portland Cement shall comply with:

- ASTM C150 Type I

- BS EN 197-1

- Sudanese standards where applicable.

Cement older than three months from the date of manufacturing shall not be used.

### Aggregates

Aggregates shall comply with ASTM C33.

Maximum aggregate size:

- 20 mm for reinforced concrete.

- 10 mm for repair works and toppings.

### Reinforcement

High-yield deformed bars:

- fy = 460 MPa minimum.

Steel shall be free from:

- oil

- mud

- loose rust

- paint

## Concrete Strength

| Application | Minimum Strength |
| --- | --- |
| Blinding | C15 |
| Manholes | C20 |
| Septic tanks | C25 |
| Structural repair works | C25 |
| Water tank supports | C25 |

## Testing

The Contractor shall provide:

- Slump test for every pour.

- Six concrete cubes for every 50 m³.

- 7-day and 28-day compressive strength tests.

- Crushing Reports: All data provided by the independent testing facility must log the failure load in Kilonewtons (kN), the surface area of the test specimen in square millimeters (mm²), and the final calculated strength converted precisely into N/mm².

- Non-Compliance: Any sample batch registering a crushing strength below 30 N/mm² at the 28-day interval will be flagged as a structural failure, prompting immediate halting of subsequent works and mandatory core-testing.

## Execution, Workmanship, and Quality Control

- Mechanical Compaction: Immediately following placement, all fresh concrete must be thoroughly compacted around the steel reinforcement mesh using mechanical needle vibrators to eliminate air pockets, honeycombing, and voids.

- Curing Requirements: Exposed concrete surfaces must be kept continuously damp via continuous water spraying or ponding system to ensure slow hydration and prevent shrinkage cracks until the 30 N/mm² design strength is achieved.

- Engineering Clearance: No concrete pouring shall begin until the supervising engineer checks and signs off on the formwork alignment, rigid bracing, cleanliness, and structural steel reinforcement spacing.

## Hot-Weather Concreting

### General Requirements

- Standard Compliance: All concrete works executed during hot weather conditions shall strictly comply with the technical frameworks of BS EN 206 and BS 8500.

- Applicability: This clause applies to all in-situ concrete works irrespective of individual element volume or mix.

### Temperature Controls & Materials

- Concrete Discharge Temperature: The temperature of fresh concrete at the point of discharge shall not exceed 35°C, unless specialized, engineer-approved cooling measures are implemented.

- Cement Storage and Delivery Temperature: Cement powder at the time of mixing shall not exceed 80°C. Bagged cement must be stored in a shaded, well-ventilated weatherproof structure, elevated off the ground, and protected from direct solar heat gain to prevent flash setting and thermal cracking.

- Pre-cooling Measures: The Contractor shall utilize chilled batch water, flake ice, or shaded aggregate stockpiles to maintain the specified temperature thresholds.

### Execution & Placement

- Substrate Preparation: Formwork, reinforcement, and subgrades shall be thoroughly pre-wetted with cool water immediately prior to placement to prevent the rapid absorption of mix water.

- Scheduling Restrictions: Concrete placement shall be rescheduled to cooler periods of the day (early morning or night) if ambient temperatures jeopardize setting times or workability.

- Delivery Timeframes: Transit and waiting times for ready-mix concrete delivery trucks shall be minimized to prevent premature slump loss.

### Curing and Protection

- Initial Curing: Curing operations must commence immediately following final finishing preventing plastic shrinkage cracking caused by high evaporation rates.

Method & Duration: Continuous wet curing (moist burlap/ponding) or approved chemical curing membranes shall be maintained for a minimum of 7 consecutive days.

## Division 07 –Waterproofing and Roof Protection

## 2.1 Roof Slope Screed

Roof screed (Khafjah) indicated in the BOQ shall:

- Achieve minimum slope of 1:40;

- Use cement: sand ratio of 1:3;

- have minimum thickness of 40 mm at high points;

- Contain waterproofing admixture approved by the Engineer.

- The surface shall be free from ponding after completion.

- Maximum standing water after rainfall is 5 mm.

## 2.2 Acrylic Waterproofing System

The acrylic waterproofing system referenced in the BOQ shall be equivalent to:

- Mixguard AC,

- SikaTop Seal 107,

- Ceresit CR166, or

- Approved equivalent.

Properties:

- Crack bridging.

- Flexible.

- UV resistant.

- Suitable for Sudan climate.

Application:

- Minimum two coats.

- Total dry film thickness not less than 2 mm.

## 2.3 Flood Testing

Completed waterproofed areas shall undergo:

- 72-hour ponding test.

Acceptance Criteria:

- No leakage;

- No dampness;

- No visible deterioration.

## Division 08 – Doors, Windows and Metal Works

## 3.1 Steel Doors

Steel doors shall comprise:

Frame

- RHS 40 × 80 × 2 mm.

- Fully welded.

Door Leaf

- RHS 30 × 60 × 2 mm.

- 1.2 mm minimum steel sheet.

- Internal stiffeners at maximum 400 mm spacing.

## 3.2 Finishing

All steelwork shall receive:

- One zinc-rich primer coat;

- Two anti-rust coats;

- Two enamel finishing coats.

Dry film thickness:

- Minimum 100 microns.

## 3.3 Aluminum Windows

Aluminum sections shall:

- Minimum 1.4 mm thickness;

- Powder-coated finish;

- 60–80 micron coating thickness.

Glass:

- Minimum 6 mm clear glazing.

  - Technical Specifications

  - Pre-Installation Iron Framing

- Material Profile: High-tensile structural steel rectangular hollow sections (RHS) measuring 80mm × 40mm (8cm × 4cm).

- Treatment: Shop-applied anti-corrosive red-oxide primer layer before structural installation into masonry surrounds.

  - Passageways, Operation Rooms, and Bathrooms, Doors & Windows

- Aluminum Extrusions: Genuine Saudi aluminum architectural profiles featuring a 2mm material wall thickness.

- Glazing (Glass Panels): 6mm thick, tempered or high-strength architectural tinted glass, set with premium EPDM rubber gaskets.

- Hardware & Accessories:

  - Heavy-duty commercial hydraulic door closers configured with adjustable latching speeds.

  - Stainless steel institutional handles, heavy-gauge commercial locksets, and perimeter trim.

  - Heavy-duty ball-bearing sliding track assemblies for the operation room doors.

- Size Variations (Doors):

  - Standard Passageway/Zone Doors: 2.0m × 2.2m | 2.7m × 2.2m | 1.4m × 2.2m | 1.0m × 2.2m | or as in BOQ.

  - Bathroom Doors: 0.80m × 2.2m

  - Operation Room Doors (Sliding Type): 1.5m × 2.2m

- Size Variations (Windows):

  - Standard Architectural Windows: 1.4m × 1.8m | 3.0m × 2.0m | or as in BOQ

  - Aluminum Skylight Assemblies

- Structural Frame: Built from 2mm thick aluminum profiles matching the performance properties of structural windows.

- Glazing: Weatherproof, high-impact 6mm tinted safety glass featuring UV-resistant commercial perimeter sealants.

- Size Variations (Skylights):

  - Staircase Skylights: 0.80m × 1.2m

  - Corridor/Zone Skylights: 0.40m × 2.0m

  - Bathroom Skylights: 0.60m × 0.60m

  - Ward Partitions

- Profile System: Aluminum structural sections featuring a heavy 4mm profile wall thickness.

- Assembly Elements: Supplied complete with institutional floor/wall fixing bolts, internal privacy panels/glazing, structural connectors, and heavy-duty handles.

  - Execution, Workmanship, and Quality Control

- On-Site Dimensions: The contractor must verify all structural opening sizes on-site prior to completing factory assembly of the aluminum frames. No spacing gaps greater than 5 mm between the steel sub-frame and aluminum frame are permitted.

- Glazing Standards: All 6 mm tinted glass panels must be set inside the aluminum channels using continuous, high-grade EPDM rubber gaskets. Silicone sealants must be applied cleanly along the external perimeter to ensure absolute wind and water tightness.

- Plumb and Level Tolerances: Erect all frames perfectly vertical and level. The maximum allowable installation deviation is 1 mm per meter of height. Diagonal measurements of completed frames must be identical to guarantee perfect squareness.

- Hardware Adjustment: Adjust all automatic door closers and sliding tracks so that doors operate smoothly without requiring excessive force, and latch securely without rattling.

- Protection and Cleaning: Keep all protective factory plastic wrap on the aluminum profiles until final handover. Clean away all structural mortar, plaster splashes, or silicone streaks from the glass and metal surfaces using non-abrasive, non-acidic cleaning agents.

  - Technical Specifications (Metal Works)

    - Security Grilles (Windows, Skylights, and Secondary Exterior Doors)

- External Perimeter Frame: Heavy-duty, structural steel rectangular hollow section (RHS) pipes measuring 80mm × 40mm (minimum wall thickness 2.0mm).

- Internal Vertical Elements: Structural steel RHS pipes measuring 60mm × 30mm, arrayed vertically with a maximum clear spacing of 200mm center-to-center.

- Internal Horizontal Elements: Structural steel RHS pipes measuring 80mm × 40mm, positioned horizontally every 700mm to form a rigid geometric pentagonal pattern.

- Fastening Hardware: Heavy-duty tamper-proof masonry expansion bolts or chemically anchored steel pins driven at least 80mm deep into concrete structural surrounds.

  - Staircase Handrails

- Material Composition: Industrial-grade stainless steel (Grade 304 or higher) or heavy-gauge galvanized structural steel pipe profiles.

- Dimensions: Ergonomic top rail diameter between 38mm and 50mm, positioned at a finished height of 900mm to 1000mm measured vertically from the stair tread nosing.

- Structural Supports: Fixed stanchions/posts spaced at a maximum interval of 1200mm, firmly anchored directly into the structural concrete staircase base plates or side walls.

  - Corrugated Iron Doors (Rooftop & Main Entrance doors)

- Rooftop Staircase Door (1.0m × 2.2m):

  - Skin: Heavy-gauge, weather-resistant galvanized corrugated iron sheeting (minimum 1.2mm thickness) welded to a rigid internal square structural steel chassis.

  - Hardware: Weatherproof, heavy-duty commercial mortise locksets, stainless steel pull handles, and a minimum of three heavy-duty bullet hinges.

- Main Entrance Door (3.0m × 2.2m):

  - Configuration: Double-leaf structural iron gate matching the 2.2-meter clearance, constructed from high-tensile corrugated iron sheets integrated with structural internal bracing.

  - Hardware: Heavy-duty industrial slide bolts (top and bottom drop-bolts), high-security institutional padlock eyes, commercial pull bars, and structural-grade pivoting hinges.

    - Paint & Protective Finishes

- Primer Base: Minimum of two (2) separate coats of high-performance zinc-chromate or red-oxide anti-corrosive structural metal primer.

- Finish Coat: Minimum of two (2) coats of premium poly-urethane or industrial-grade gloss enamel paint designed for heavy UV exposure and frequent chemical washing.

  - Execution & Finishing Workmanship

- Welding: All structural joints must be fully, continuously welded (no spot welding allowed). All welds must be ground smooth, flush, and free of slag or pinholes before painting.

- Plumb & Square Alignment: Install all doors, security frames, and handrails perfectly true, level, and vertically plumb, holding tolerances within a strict ±2mm variance.

- Ergonomic Safety: Ensure all staircase handrail terminations are cleanly returned smooth into the structural wall surface or dropped down to the floor to prevent clothing snags.

- Anti-Corrosion Priming: All steel surfaces must be thoroughly de-rusted, degreased, and treated with at least two coats of zinc-phosphate anti-corrosive primer before leaving the fabrication workshop.

- Tolerances: Frames must be installed strictly plumb and square. Maximum allowable deviation across structural heights is ±2 mm.

- Supervising Engineer Approval: Present the final installed grilles, handrails, and entrance assemblies for close joint inspection and official written sign-off.

## 4. Plastering Technical Specifications

  - Material Requirements

- Cement: Premium-quality Ordinary Portland Cement (OPC) free from lumps, moisture, or premature setting.

- Sand: Clean, sharp, well-graded fine river sand, screened to remove clay, loam, shells, organic particles, or chemical impurities.

- Expanded Metal Mesh (Expanda): High-tensile, corrosion-resistant galvanized expanded steel mesh sheet with a minimum width of 30 cm to 40 cm.

- Water: Fresh, potable, clean, and completely free from harmful oils, acids, alkalis, or organic matter.

  - Exterior Plastering (2 cm Thick)

- Application Areas: Exterior walls, inner and outer faces of the roof parapets, and all faces of the stairwell structure.

- Mix Ratio: Strictly 1:6 by volume (1 part cement to 6 parts screened sand).

- Thickness: Applied to a uniform, flat, and plumb total thickness of 2 cm.

- Finish Style: Perfectly smooth, level surface achieved via timber floats and steel trowels. No trowel marks, waves, or surface ripples are permitted.

- Tight Area Integration: Plaster neatly flush up to external electrical junction boxes, switches, and utility fixtures. Maintain sharp, square, orthogonal corners without any messy over-spill.

  - Structural Crack Remediation Method

- Plaster Removal: Chip away and entirely remove the failing, cracked plaster down to the bare red brick masonry substrate. The removal strip must expose at least 15 cm to 20 cm (150–200 mm) of clean masonry on both left and right sides of the crack line.

- Surface Cleaning: Brush away loose dust, mortar fragments, and debris from the exposed masonry channel, then moisten the surface thoroughly.

- Mesh Installation: Position and securely fasten the expanded metal mesh (Expanda) centrally over the crack using galvanized masonry nails or pins. The mesh must extend a minimum of 150 mm to 200 mm past the crack boundary on both sides to distribute tensile stresses.

- Replastering: Apply a primary bonding coat, followed by the finishing plaster coat, ensuring the new surface matches the plane, texture, and level of the surrounding existing plaster perfectly.

  - Execution, Workmanship, and Quality Control

- Scaffolding Safety: Erect independent, rigid external tubular scaffolding fitted with secure working platforms, toe boards, and catch nets along the building perimeter.

- Engineering Sign-off: Do not apply mesh or plaster over cracked zones until the supervising engineer inspects the cleaned masonry substrate and approves the structural preparation.

- Water Curing: Keep all newly applied exterior plaster and repaired crack patches continuously damp by spraying with water at least twice daily for a minimum period of 7 days post-construction to ensure proper hydration and prevent shrinkage cracks.

- Weather Restrictions: Do not apply cement plaster during heavy rain, high winds, or ambient temperatures exceeding 40°C to avoid premature drying or wash-outs.

## Division 09 – Finishes

  - Ceramic Wall Tiles

Applicable to:

- toilets;

- bathrooms;

- wash areas;

- sanitary rooms.

Requirements:

- Water absorption ≤ 3%.

- Minimum thickness 8 mm.

Installation:

- Cement adhesive C2 grade.

- Joint width 2–3 mm.

  - Porcelain Floor Tiles

Porcelain tiles shall be:

- Fully vitrified;

- Water absorption <0.5%;

- Minimum thickness 10 mm.

Slip resistance:

- R10 minimum.

Wet areas:

- R11 minimum.

  - Tile Testing

Lippage:

- maximum 1 mm.

Hollow sounding areas:

- maximum 5% of room area.

Defective tiles shall be replaced.

  - Technical Specifications (Tiling Works)

    - General Workmanship and Material Cutting

- Edge Precision: All tile cutting must be done using professional wet-saw mechanical cutters to ensure perfectly straight, crisp, unchipped edges. Hand-snapping or jagged manual cuts are strictly prohibited.

- Grouting & Expansion: All joints must be fully packed with a uniform slurry of premium white cement or an approved color-matched grout. Any excess grout must be wiped clean with a damp sponge before it sets.

- Layout Symmetry: Tile layouts must be planned from the center of each room or corridor to ensure balanced, equal-sized cut tiles along the perimeter boundaries.

    - Porcelain Tiling (Rooms and Corridors)

- Flooring: Supply and install premium-grade 60 × 60 cm porcelain tiles. Tiles must be bedded on a true-to-level layer of 1:4 cement mortar (1 part cement to 4 parts dry sand). Surfaces must be checked continuously with a spirit level to ensure a completely flat finish with zero lippage.

- Skirting: Supply and install matching porcelain skirting boards cut to a uniform height of 10 cm along all room and corridor perimeters. Skirting must be installed perfectly flush or with a uniform protrusion as approved by the engineer, with top edges smoothly grouted.

    - Bathroom Ceramic Tiling

- Bathroom Floors: Supply and install high-quality Egyptian ceramic tiles measuring 30 × 30 cm. These must be bedded on a 1:4 cement mortar mix. The installer must maintain a strict, uniform slope falling toward the floor drainage traps to guarantee that no water ponds on the floor.

- Bathroom Walls: Supply and install matching Egyptian ceramic wall tiles measuring 50 × 30 cm. Tiles must be fixed perfectly plumb using a thin-set mortar or approved tile adhesive over a rough plaster scratch coat, maintaining perfectly aligned horizontal and vertical grout lines.

    - Natural Marble Works (Staircases and Entrances)

- Internal Staircase Steps: Supply, cut, and install premium natural marble slabs for the internal staircase steps. The steps must feature a clear width of 1.0 meter, incorporating both the horizontal treads and vertical risers. Slabs must be selected for uniform color, pattern, and grain continuity.

- Internal Staircase Landings: Supply and install matching natural marble slabs for the internal staircase landing zones, ensuring the bedding is perfectly level and flush with the incoming step flights.

- Entrance Staircase Landing: Supply and install heavy-duty natural marble slabs for the main outdoor entrance staircase landing, ensuring a microscopic outward slope to prevent exterior rain puddle formation.

- Entrance Wall Cladding: Supply and install premium natural marble cladding slabs across the walls of the main entrance lobby. Marble panels must be secured using a combination of structural bedding mortar and mechanical stainless-steel anchors or clips to ensure permanent vertical stability.

    - External Courtyard Tiling

- Courtyard Floors: Supply and install durable, weather-resistant Egyptian ceramic tiles measuring 40 × 40 cm. Tiles must be bedded on a 1:4 cement mortar layer over a well-compacted sub-base or external concrete apron.

- Slope and Drainage: All courtyard tiling must be precisely sloped toward external storm-water drainage channels or gully traps to ensure efficient surface water runoff during heavy rainfall.

  - Execution, Workmanship, and Quality Control

- Substrate Preparation: Before applying mortar, all concrete floors must be thoroughly swept clean of dust, oil, paint drops, or loose plaster. The bare concrete must be lightly wetted with clean water to prevent it from rapidly absorbing the mixing water from the fresh mortar bed.

- Leveling and Alignment Checks: The contractor must use laser levels or nylon line grids across all rooms and corridors. The supervising engineer will inspect the dry tile layout and leveling lines before permanent mortar setting begins.

- Protection of Finished Works: Newly tiled floors must be barred from all foot traffic for a minimum of 24 hours post-installation. Completed flooring must be covered with protective heavy-duty canvas, building paper, or plastic sheets to prevent scratching or chipping during subsequent construction activities.

- Final Cleansing: Upon completion of all grouting and curing phases, all tiled surfaces must be thoroughly washed with clean water and mild, non-acidic detergents to remove film, dust, and stubborn mortar stains, leaving a flawless, ready-for-handover finish.

## Painting

Internal Paint

Acrylic emulsion.

Properties:

- washable;

- anti-fungal;

- low VOC.

Minimum:

- one primer coat;

- two finishing coats.

External Paint

Weather-shield acrylic system:

- UV resistant;

- water resistant;

- anti-carbonation.

Minimum:

- one sealer coat;

- two finish coats.

  - Technical Specifications (Painting)

### 6.1.1 Material Standards and Approvals

- Paint Quality: All finishing paints must be first-grade silk paint manufactured by Jotun (e.g., Fenomastic series for interiors, Jota shield series for exteriors) or an approved equivalent premium brand.

- Sample Submission: Before any paint or putty is delivered to the job site, the contractor must apply mock-up samples (minimum 1.0 m × 1.0 m patches) on the walls for color, texture, and gloss approval by the supervising engineer.

### 6.1.2 Interior Walls Painting

- Surface Preparation: Scrap away all loose mortar, dust, and debris. Apply approved high-quality wall putty filler in successive layers. Sand down each layer with fine-grade sandpaper to achieve a perfectly flat, uniform, and plumb surface.

- Application System: Apply one base primer coat followed by three (3) separate coats of premium plastic emulsion silk paint. Each coat must be allowed to dry completely and be lightly sanded before the next coat is applied. The final surface must be free of brush marks, roller stipples, runs, or color variations.

### 6.1.3 Exterior Walls, Stairwells, and Parapet Walls Painting

- Surface Preparation: Level all rough concrete and masonry substrates using a structural sand-cement mortar rendering coat. Fill all minor voids, blowholes, and surface honeycombing to ensure a uniform plane.

- Application System: Apply a specialized exterior alkali-resistant primer coat, followed by three (3) separate coats of premium weatherproof exterior silk paint. The final finish must provide robust UV protection and resistance to environmental weathering.

### 6.1.4  Room and Corridor Ceilings Painting

- Surface Preparation: Clean all ceiling concrete surfaces, remove formwork release oils, and apply a thin layer of specialized ceiling putty or joint compound to eliminate imperfections. Sand smoothly.

- Application System: Apply one primer coat followed by three (3) separate coats of premium plastic emulsion paint, matching the exact surface execution and seamless finish required for the interior walls.

### 6.1.5 Execution, Workmanship, and Quality Control

- Protection of Fixtures: Prior to starting any preparation or painting, the contractor must completely mask and protect all floors, electrical boxes, windows, door frames, and completed plaster works using plastic sheeting and masking tape.

- Drying Time Intermissions: The contractor must strictly adhere to the manufacturer’s data sheets regarding drying times between successive coats. No subsequent coat shall be applied until the supervising engineer inspects and approves the previous layer.

- Environmental Constraints: Do not apply exterior paint during dusty conditions, high winds, rain, or when ambient temperatures exceed the maximum limits specified by Jotun (typically 40°C).

- Final Lighting Inspection: The final finished paintwork will be inspected under cross-lighting conditions. Any visible patches, waves, transparency issues, or uneven gloss must be corrected by the contractor at their own expense.

## Technical Specifications (Epoxy)Material Requirements

- Epoxy Paint System: Must be a high-build, self-leveling, fiber-reinforced epoxy coating system (such as Epoxy Fiber or an approved medical-grade equivalent) designed for heavy foot traffic, chemical resistance, and sterile environments.

- Performance Attributes: The cured system must be completely seamless, non-porous, antibacterial, easy to sanitize, and resistant to medical disinfectants, blood, and laboratory chemicals. It must achieve a minimum compressive strength of 50 N/mm² to withstand medical equipment loads.

  - Substrate and Surface Preparation

- Mechanical Profiling: The underlying concrete slab must be thoroughly clean, structurally sound, and completely dry (moisture content must not exceed 4% when tested with a calcium chloride or digital moisture meter).

- Remediation: Use mechanical floor grinders equipped with dust-extraction vacuums to remove all curing compounds, laitance, old paint, oils, and grease. Blowholes, cracks, and surface pits must be filled flush using an approved solvent-free epoxy putty repair compound.

- Priming: Apply one uniform coat of a high-penetration epoxy primer to seal the concrete pores and ensure maximum chemical bonding between the substrate and the subsequent epoxy coats.

  - Epoxy Application and Execution

- First Coat Application: Once the primer has cured to a tack-free state, mix the fiber-reinforced epoxy components strictly according to the manufacturer’s instructions using a low-speed mechanical mixer. Apply the first coat uniformly using a notched squeegee or lint-free roller in a single direction (e.g., East-West).

- Second Coat Application: Allow the first coat to dry within the manufacturer's specified recoat window. Apply the second coat exactly perpendicular to the first coat (e.g., North-South). This cross-directional roll ensures a perfectly level surface, uniform thickness, and eliminates any potential pinholes or tracking marks.

- Final Finish: The completed floor system must cure to a perfectly smooth, level, satin or gloss finish with a total dry film thickness (DFT) that complies with the manufacturer's heavy-duty medical traffic data sheets.

  - Execution, Workmanship, and Quality Control

- Dust and Contamination Control: Because these are medical delivery, nursery, and laboratory spaces, the application area must be completely sealed off using plastic sheeting isolation barriers. No dust, insects, or floating airborne particles are permitted in the rooms during the application and curing phases.

- Cove Base Integration (Sanitary Detailing): At the junctions where the floor meets the walls, the epoxy must be turned up the wall to create a seamless, radiused cove skirting (typically 10 cm to 15 cm high) if required by the clinical design, eliminating sharp 90-degree corners where bacteria can accumulate.

- Curing Timeline: The treated rooms must be kept under strict climate control (ideally between 15°C and 30°C) and completely locked down. Light foot traffic is restricted for at least 24 hours, and heavy mechanical equipment or medical furniture installation must not occur until a full 7-day chemical cure is reached.

- Testing and Inspection: The supervising engineer will inspect the final cured floor for levelness, complete opacity, the total absence of air bubbles, blisters, or roller lint, and absolute adhesion to the substrate before handover.

## Division 22 – Water Supply and Plumbing

  - PPR Water Piping

The BOQ requires German-manufactured PPR pipe systems.

Acceptable standards:

- DIN 8077

- DIN 8078

Pressure Class:

| Service | Rating |
| --- | --- |
| Cold Water | PN16 |
| Hot Water | PN20 |

  - Pipe Installation

Joining method:

- thermal fusion only.

Threaded connections shall not be used except at equipment interfaces.

Pipe supports:

| Pipe Diameter | Maximum Spacing |
| --- | --- |
| 20-25 mm | 1.0 m |
| 32-50 mm | 1.5 m |
| 63 mm+ | 2.0 m |

  - Pressure Testing

Hydrostatic test pressure:

- 1.5 times working pressure.

Test duration:

- 2 hours minimum.

Acceptance:

- zero visible leakage;

- pressure loss less than 5%.

  - Division 22.4 UPVC Drainage System

Drainage pipes shall be:

- UPVC Schedule 80;

- solvent welded.

Minimum diameters:

| Service | Diameter |
| --- | --- |
| Basin | 50 mm |
| Floor drain | 75 mm |
| WC branch | 110 mm |
| Main sewer | 160 mm |

  - Sanitary Fixtures

Western WC

- Vitreous china.

- Dual flush.

- Maximum flush 4.5 liters.

  - Squat WC

- Vitreous china.

- Heavy-duty hospital grade.

- Slip-resistant footrests.

  - Wash Basins

- Vitreous china.

- Wall mounted.

- Chrome plated mixer.

Working pressure:

- 1-6 bar.

  - Division 22.6 Water Storage Tanks

The BOQ includes 2000-liter storage tanks with booster systems.

Tank requirements:

- UV stabilized polyethylene.

- Triple-layer construction.

- Food-grade material.

The tank shall be mounted on:

- galvanized steel support frame.

Design load:

- full water load + 25% safety factor.

  - Division 22.7 Booster Pumps

Pump body:

- stainless steel AISI 304.

Impellers:

- stainless steel.

Motor:

- IP55 minimum.

Control panel shall include:

- dry run protection;

- overload protection;

- automatic operation.

  - Division 22.8 Septic Tank Construction

The septic tank identified in the BOQ shall be constructed using reinforced concrete.

Internal walls:

- minimum 200 mm thick.

Concrete:

- C25 minimum.

Waterproofing:

- internal cementitious waterproof coating.

  - Testing

Before acceptance:

- fill with water;

- retain water for 72 hours.

Permitted leakage:

- none.

  - Division 22.9 Soak-Away Pit

The soak-away pit shall:

- be 2 m diameter;

- reach approved depth;

- be lined with masonry or reinforced concrete rings as approved by Engineer.

Surrounding filter media:

- graded crushed stone 25-75 mm.

## Division 23 – HVAC

    - Split Air Conditioning Units

Units shall:

- be inverter type;

- operate at ambient temperatures up to 52°C;

- use R32 refrigerant or approved equivalent.

Minimum EER:

- 3.2

    - Copper Pipework

Copper tubing:

- ASTM B280.

Insulation:

- closed-cell elastomeric insulation;

- minimum thickness 13 mm.

  - Commissioning

Contractor shall perform:

- nitrogen pressure test;

- vacuum test;

- refrigerant charge verification;

- 4-hour operational test.

## Division  Electrical Works

    - Wiring

Conductors:

- stranded copper;

- PVC/XLPE insulated;

- 600/1000 V rated.

Minimum cable sizes:

| Circuit | Minimum Size |
| --- | --- |
| Lighting | 2.5 mm² |
| Socket outlets | 4 mm² |
| AC circuits | 6 mm² |

    - Distribution Boards

Distribution boards shall:

- be powder-coated steel;

- IP54 minimum;

- include lockable doors;

- include circuit schedules.

    - Earthing

Earth roads:

- copper-bonded steel;

- length 3 m minimum.

Maximum earth resistance:

- 5 Ohms.

    - Testing

The Contractor shall submit certified test reports for:

- Continuity testing.

- Insulation resistance testing.

- Earth resistance testing.

- RCD testing.

- Functional testing.

  - Technical Specifications (Electrical Works)

  - Distribution Equipment and Switches

- Main Distribution Board (MDB): Supply and install a 24-way metal-clad distribution board. The board must feature factory-fitted copper busbars, neutral bars, and isolated earth bars. It must be equipped with a matching 100 Amp safety switch (main circuit breaker) providing over-current and short-circuit protection.

- Power Sockets: Supply and install premium-grade Tenby brand flush-mounted accessories. This includes 13 Amp switched shuttered socket outlets for general ring/radial power circuits and 16 Amp socket outlets for dedicated heavy-appliance radial circuits.

- A/C Isolators: Supply and install Tenby 45 Amp double-pole (DP) water heater style switches fitted with neon indicators to serve as local isolation switches for all air conditioning units.

  - Lighting and Ventilation Systems

- Room and Hallway Lighting: Supply and install 4-foot Philips fluorescent/Neon light fixtures, complete with electronic ballasts, starter mechanisms, high-efficiency tubes, localized switches, and intermediate wiring connections.

- Bathroom Lighting: Supply and install 2-foot English-made fluorescent/Neon ceiling light fixtures. These units must feature vapor-proof or moisture-resistant enclosures suitable for damp bathroom environments.

- Operating Room Lighting: Supply and install high-intensity, specialized flood lights designed specifically for medical operating rooms. These fixtures must provide shadowless, high-color-rendering illumination, and be safely wired to dedicated clean-power circuits.

- Ceiling Fans: Supply and install heavy-duty 56-inch ceiling fans, including down rods, safety hooks, motor assemblies, wiring, and matching multi-step speed wall regulators.

- Wall Fans: Supply and install Orient (Indian make) wall-mounted mechanical fans, complete with swivel-oscillation mechanisms, pull-cord or digital controls, mounting brackets, and local power connections.

- Exhaust Ventilation: Supply and install heavy-duty mechanical exhaust fans for all bathroom and laboratory spaces to ensure proper air changes. Laboratory units must be chemically resistant if specified by the layout.

  - Air Conditioning and HVAC Infrastructure

- Window A/C Units: Supply and install O General Window brand (or approved equivalent) Freon air conditioning units in designated wall sleeves. Available in two capacities: 24,000 BTU and 18,000 BTU.

- Split A/C Units: Supply and install O General brand (or approved equivalent) split-type air conditioning units comprising indoor high-wall evaporators and outdoor condensing units. Available in two capacities: 24,000 BTU and 18,000 BTU.

- HVAC Connections and Drainage: All A/C installations must include structural mounting brackets, refrigerant copper piping insulated with elastomeric foam, interlocking control wiring, and a dedicated uPVC condensate drain pipe routed with a continuous downward slope connected to the nearest return water or greywater drainage point.

## Division  – Medical Waste Incinerator

  - General

The medical waste incinerator specified in the BOQ shall be suitable for treatment of infectious healthcare waste.

  - Combustion Requirements

Primary chamber:

- minimum 800°C.

Secondary chamber:

- minimum 1100°C.

Residence time:

- minimum 2 seconds.

  - Refractory Lining

High-alumina refractory brick:

- minimum thickness 114 mm.

Insulating layer:

- minimum 50 mm ceramic insulation.

  - Chimney

Material:

- stainless steel.

Height:

- Minimum 6 m above finished ground level.

  - Testing

The Contractor shall undertake:

- dry commissioning;

- operational commissioning;

- trial burn test;

- temperature verification.

  - Construction of a Medical Waste Incinerator

  - Technical Specifications

    - Dimensions & Geometric Footprint

- Base Area Footprint: 2500 mm × 2500 mm overall outer dimension at ground level.

- Structural Vertical Height: 2720 mm overall height measured from the natural ground line to the concrete slab roof cap (excluding the vertical extension of the metal chimney).

- Operating Capacities: Designed as a natural-draught dual-chamber configuration with a nominal throughput capacity matching localized clinical demands (~12 to 15 kg/hour).

    - Civil & Concrete Substructure Works

- Mass Concrete Foundation: Cast an unreinforced or minimally reinforced structural foundation slab measuring 2500×2500 mm with an overall vertical thickness/depth of 650 mm.

- Concrete Strength Specification: Grade C20/25 nominal mix (1:2:4 ratio by volume) using pure Portland Cement, clean potable water, well-graded coarse aggregates (maximum aggregate size 20 mm), and washed river sand.

- Ash Pit Profile: Integrated directly below the primary combustion chamber, featuring smooth cement mortar rendering along internal faces to facilitate frictionless ash removal using long-handled scrapers.

- Concrete Access Steps: Monolithically cast concrete step structures provided at the designated loading bay face to afford operators an ergonomic, safe platform height during waste charging sequences.

    - Masonry & Thermal Barrier Linings

- Primary Combustion Chamber Lining: Inner chamber surfaces exposed directly to active flames must be lined with premium refractory firebricks capable of withstanding continuous operational temperatures exceeding 850°C to 1100°C.

- Refractory Mortar Jointing: All firebricks must be laid exclusively with high-temperature refractory fireclay mortar (composed of premixed calcium-aluminate cement or specialized kaolin clays) with tight joints not exceeding 3 mm thickness.

- Exterior Protective Envelope: The outer structural walls above ground level shall be constructed using high-quality, well-burnt solid local clay bricks (1.5-brick thick layout configuration) laid in a highly workable 1:4 cement-to-sand mortar matrix, meticulously plumbed, joint-struck, and cured.

    - Metallurgical, Chimney & Metalwork Assemblies

- Exhaust Chimney Stack: Supply, fabricate, and install a vertical high-clearance exhaust chimney stack mounted securely through the top concrete roof slab.

  - Material: Minimum 4 mm thick heat-resistant mild steel or stainless steel pipe.

  - Diameter: Minimum 150 mm inside diameter (or as detailed on the approved UNOPS reference drawings).

  - Height: The stack must rise to a minimum vertical clearance of 4 to 5 meters above the concrete slab cap to ensure proper natural draught and safe dispersion of emissions.

  - Accessories: The chimney must be topped with an integrated conical rainwater cowl (spark arrestor) and rigidly anchored using high-tensile guy wires or welded structural steel support brackets to withstand local wind loads.

- Combustion Metal Grill (Grate): Fabricated using high-grade, heat-resistant cast iron or solid steel bars (minimum 20 mm diameter), spaced at 50 mm intervals center-to-center to endure intense thermal cycling without warping.

- Loading & Ash Clean-Out Doors: Formed from heavy-gauge, minimum 4 mm thick structural mild steel plates backed by dense ceramic fiber insulation blankets. Both doors must feature counterweighted hinge mechanisms and tight-fitting latches to ensure a complete, airtight secondary chamber seal.

  - Execution, Workmanship, and Quality Control

- Refractory Curing Intermission: Following the completion of the firebrick masonry and refractory mortar lining, the structural shell must be allowed to dry naturally for at least 7 to 14 days. The contractor must then execute a controlled, slow-temperature wood-fire preheating phase to drive out residual moisture and cure the mortar bonds before full high-temperature operation.

- Metalwork Thermal Expansion: All internal structural steel supports, metal grills, and door frames must be installed with explicit expansion joints (minimum 10 mm to 15 mm clear gap packed with ceramic fiber rope) to prevent the steel from buckling or cracking the brickwork when expanding at high temperatures.

- Emissions and Draft Verification: The supervising engineer will conduct an initial operational trial run using standard test waste to verify that the mechanical charging doors lock tightly, the chimney stack draws exhaust smoothly without smoke backing out, and the ash pit doors maintain an airtight seal.

- Anti-Corrosion Painting: All external, non-insulated structural steel elements, door hinges, latch mechanisms, and the chimney stack base must be cleaned of mill scale and finished with two coats of high-temperature silicone-based aluminum paint capable of resisting temperatures up to 600°C.

## Appendix X: Handover Documentation and Final Deliverables

Upon completion of all rehabilitation works, the Contractor shall submit a complete set of handover documentation to the Engineer and the Employer. The submission shall demonstrate that all works have been executed, tested, commissioned, and completed in accordance with the Contract Documents, approved drawings, technical specifications, applicable standards, and the Engineer's instructions.

The Contractor shall be responsible for compiling, organizing, and submitting all required records and documents in both hard-copy and electronic formats. All documents shall be provided in clear, legible, and professionally organized form.

## As-Built Documentation

The Contractor shall prepare and submit comprehensive As-Built Drawings reflecting the actual works constructed on site. The drawings shall include, but not be limited to:

- Architectural layouts and modifications.

- Structural rehabilitation and repair works.

- Water supply systems and pipe networks.

- Sanitary and drainage systems.

- Septic tanks, manholes, inspection chambers, and related infrastructure.

- Electrical installations and distribution systems.

- HVAC systems, where applicable.

- Medical waste management facilities and incinerator installations, where applicable.

- External works and site infrastructure.

As-built drawings shall clearly indicate all deviations from the original design and shall be certified by the Contractor prior to submission.

## Testing and Commissioning Records

The Contractor shall submit complete testing and commissioning records for all installed and rehabilitated systems, including:

- Water supply network testing reports.

- Plumbing pressure testing reports.

- Drainage and sanitary system testing reports.

- Septic tank water-tightness testing reports.

- Electrical testing and commissioning reports.

- Earthing and electrical protection test certificates.

- Lighting performance and functional testing reports.

- HVAC commissioning records.

- Equipment start-up and operational testing reports.

- Medical waste incinerator commissioning and operational verification reports, where applicable.

All reports shall be signed by qualified personnel and approved by the Engineer.

## 11.3 Quality Assurance and Quality Control Records

The Contractor shall submit all quality documentation generated during project implementation, including:

- Material approval records.

- Factory certificates and manufacturer's compliance certificates.

- Laboratory test reports.

- Inspection and approval records.

- Non-conformance reports and corrective actions undertaken.

- Quality checklists.

## 11.4 Operation and Maintenance Manuals

The Contractor shall provide complete Operation and Maintenance (O&M) Manuals for all installed equipment, systems, and facilities.

The manuals shall include:

- Description of equipment.

- Manufacturer's data sheets.

- Operating procedures.

- Preventive maintenance requirements.

- Recommended maintenance schedules.

- Troubleshooting procedures.

- Spare parts lists.

- Safety precautions.

- Warranty information.

- Supplier and manufacturer contact details.

Manuals shall be provided in English and, where requested by the Employer, key operational instructions shall also be provided in Arabic.

## 11.5 Training Requirements

Prior to final handover, the Contractor shall provide adequate training to hospital personnel designated by the Employer.

Training shall cover:

- Operation of water supply systems.

- Operation of electrical systems and distribution boards.

- Operation and maintenance of pumps and storage facilities.

- Use and maintenance of HVAC systems.

- Operation of medical waste incinerators and waste management facilities.

- Routine maintenance requirements for rehabilitated infrastructure.

Training records, attendance sheets, and training materials shall be submitted as part of the handover documentation.

## 11.6 Warranties and Guarantees

The Contractor shall submit all warranties, guarantees, and manufacturer certifications associated with the completed works and supplied equipment.

These shall include:

- Equipment manufacturer's warranties.

- Waterproofing system warranties.

- Electrical installation warranties.

- Pump and mechanical equipment warranties.

- HVAC equipment warranties.

- Specialized system warranties required under the Contract.

Warranty periods shall commence from the date of Taking-Over Certificate issuance unless otherwise specified in the Contract.