ANNEX 1: SCOPE OF WORK AND TECHNICAL SPECIFICATION ESTABLISHMENT OF LONG-TERM AGREEMENT FOR SERVICES

FOR Supply, installation and commissioning of hybrid solar PV generator system, Backup power supply, borehole risers, casings, pipes and fittings, including after sale service and auxiliary spare parts for UNICEF ETHIOPIA supported WASH projects across all regional states of Ethiopia- REFERENCE No.__________________

Contents 1. GENERAL SCOPE OF WORK 2 2. MOTOR PUMP UNITS AND ACCESSORIES 5 3. SOLAR PV AND ELECTRICAL SYSTEM 9 4. SYSTEM AC/DC CABLES AND ACCESSORIES 15 5. BACKUP POWER SUPPLY SOURCE SYSTEM 19 6. MAIN DISTRIBUTION PANELS AND CONTROL SYSTEM 28 7. EARTHING AND LIGHTNING PROTECTION SYSTEM 35 8. SAFETY AND SECURITY WORKS FOR PV SYSTEM 38 9. BOREHOLE CASINGS, PIPES, AND WELLHEAD ACCESSORIES 43 10. CIVIL AND STRUCTURAL RELATED WORKS 58 11. SCADA AND REMOTE MONITORING SYSTEMS 71 12. RECOMMENDED AND MANDATORY SPARE PARTS 77 ATTACHMENT: 79 Attachement-1: Bidder’s Technical Compliance Form 80 Attachement-2: Schedules: pump performance, solar PV Modules and Fencing 96

# GENERAL SCOPE OF WORK

  - GENERAL

Many existing water supply schemes rely on aging electrical submersible pumps powered by local diesel generators, as well as old submersible pumping systems that operate with low efficiency and require frequent maintenance. In many areas, the limited availability of public electricity, inadequate financial resources to procure sufficient fuel, and periodic shortages of diesel fuel in local markets result in interruptions to pump operations and water service delivery.

UNICEF Ethiopia intends to establish Long-Term Arrangement (LTA) with a capable and qualified Contractor to carry out procurement, supply, installations, configuration, testing, commission of modern hybrid Solar Photovoltaic Electrical Systems that shall replace the existing / old diesel powered pumping system support the replacement of existing/ old diesel-powered pumping systems for vulnerable communities and institutions across the regions of Ethiopia.

The Contractor shall be responsible for delivering a complete, functional, and reliable solar water pumping system, including all necessary equipment, materials, labor, supervision, transportation, testing equipment, documentation, and technical support.

Bidders shall refer to the detail ‘Bill of Quantities’ included in the annex 2 of the TOR document for the items required under the scope of work. The general scope of work includes but not limited to

Verification of sites parameters: During LTA implementation, UNICEF will provide site specific technical design specification of the water pumping stations. The offeror are encouraged to visit the sites and verify the site parameters before procurement of the solar equipment. Some pumping stations may require remeasurement of the capacities of the existing system or the extension of electrical wiring and/or plumbing system. The offeror must verify them during the LTA implementation.

- Procurement and supply: In accordance with the provided technical specification, offerors shall procure and supply components and accessories for delivering functional water pumping stations powered by the new solar electrical system and backup power sources where applicable. All components of the system must be made available to the Employer or its representative for inspection and quality assurance before their transportation to the locations for installations. Any units that fails the quality inspection against the technical specification must be replaced.

- Transportation, delivery and Installations: The Contractor shall transport the solar electrical and electro-mechanical pumping system components, backup power supply components, to the stipulated locations in this bid document. The Contractor shall perform all mechanical, electrical, structural, instrumentation, and control system installation works in accordance with approved drawings, manufacturer instructions, recognized engineering practices, and applicable standards. The offeror must repair or replace any damage to components that occurred during transportation. The offeror shall install, assemble and calibrate the components and ensure their functionality and specified output quantities.

Testing and commissioning: Upon completion, the Contractor shall demonstrate through testing and performance verification that the integrated system meets the specified water demand, flow rate, total dynamic head (TDH), energy efficiency targets, safety requirements, and operational reliability standards. Testing and Commissioning activities shall include but not be limited to: Visual inspections; Electrical continuity tests; Insulation resistance tests; Earthing and ground resistance measurements; PV array performance testing; Inverter functional testing; Pump performance testing; Generator integration and load testing; Protection system verification; Communication and monitoring system testing; Integrated system performance testing.

The Works shall only be considered compliant when: Equipment complies with approved specifications; Required certificates have been submitted; FAT and SAT requirements have been successfully completed; Installation complies with approved drawings; Performance tests demonstrate contractual performance; All deviations have received written approval;

Users’ training and After sale support: The Contractor shall also provide a minimum two-day training programme for operators and maintenance personnel Training shall combine classroom instruction and practical field demonstrations and shall cover, at a minimum: System overview and operating principles; Functions of major system components; Electrical and operational safety; Operating procedures and performance monitoring; Preventive maintenance requirements; Inspection procedures; Troubleshooting and fault diagnosis; Emergency response procedures; Reporting and record keeping. The Contractor shall also provide a minimum twelve-month warranty period covering technical support, corrective maintenance, repairs, replacement of defective components, and performance support services.

  - LOCATION

The works covered under this Long-Term Arrangement (LTA) may be implemented at various locations across Ethiopia. The exact sites, quantities, implementation schedules, and technical requirements will be identified during the LTA implementation period and communicated through individual Purchase Orders, or Work Orders.

For the purpose of preparing financial proposals, transportation rates, mobilization costs, and regional rate cards, bidders shall provide pricing applicable to the regions listed below. The regions are indicative of the geographical coverage expected under the LTA and do not constitute a commitment by UNICEF regarding the volume, frequency, or location of future assignments. Contractors shall demonstrate their capacity to mobilize personnel, equipment, materials, and services to any location within the designated regions, including urban, rural, remote, and hard-to-reach areas.

The Regions /administrative centers Covered Under the LTA include:

- Afar; Amhara; Benishangul-Gumuz; Central Ethiopia Region; Gambela; Harari; Oromia; Sidama; Somali; South Ethiopia Region; Southwest Ethiopia Region

  - SYSTEM COMPONENT DESCRIPTION

    - General

The Solar Pumping system consists of existing or new borehole and booster pumping stations with the capacity of ranging from 2.6KW to 460KW PV Module array, PV inverters installed at the module site will act as system controller, ensuring synchronization of the existing or newly supplied diesel generators or grid interfaces and PV systems. The components of the solar pumping system for each station comprise of:

- AC Motor-Pump Units (Solar Powered): AC motor-pump units are powered by solar photovoltaic (PV) systems through a solar pump inverter/controller that converts DC power from the solar panels into AC power. Depending on the application, they may consist of submersible pumps for boreholes and deep wells, surface pumps for shallow water sources, or booster pumps used to increase pressure and transfer water within distribution systems. The motor-pump unit typically includes an AC electric motor, pump assembly, impellers, shaft, bearings, seals, discharge connection, non-return valve, and power cables. These solar motor-pumps provide a reliable, energy-efficient, and low-operating-cost solution for water supply schemes and irrigation systems.

- Solar PV system and Electricals assembly: The solar PV components primarily include the PV modules, mounting structures, combiner boxes, and DC cabling that generate electricity. The electrical components include the controller/VFD, inverter, protection devices, isolators, grounding and lightning protection systems, monitoring equipment, and distribution boards that control and safeguard the operation of the solar water pumping system.

- A supplementary power system provided to ensure continuous operation of the water pumping station during periods of insufficient solar power, system maintenance, or emergencies. Depending on site requirements, it may include a factory-assembled diesel generator set or a grid power connection, together with manual or automatic transfer switches that safely and seamlessly switch the power supply between the primary solar system and the backup source

- System Cables, Electrical Protection and Accessories: The system cables, electrical protection devices, and associated accessories provide safe and reliable transmission of power from the solar PV array to the pump controller and motor-pump unit. These components typically include DC and AC power cables, DC/AC isolators for safe system isolation during operation and maintenance, circuit breakers for overload and short-circuit protection, and surge protection devices (SPDs) to safeguard equipment against lightning and voltage surges. Installation accessories may include cable trenches, cable trays, conduits, junction boxes, cable glands, connectors, earthing and grounding systems, and lightning protection equipment. Together, these components ensure system safety, operational reliability, and compliance with electrical standards.

- Borehole Headworks and Rising Main: The borehole headworks and rising main comprise the wellhead cover assembly, outlet manifold, pipes, fittings, and associated accessories that provide a secure connection at the borehole and convey water from the groundwater source to the storage reservoir or transmission system while ensuring safe, efficient, and sanitary operation.

- Transmission/Distribution Network: The transmission and distribution network consists of pipelines, valves, fittings, and appurtenances that convey water from the source or storage facilities to water points and end users, ensuring reliable, controlled, and efficient water delivery throughout the service area.

- Safety and Protection Measures: Safety and protection measures comprise all physical and operational provisions necessary to safeguard the solar pumping system and associated infrastructure from theft, vandalism, unauthorized access, and accidental damage. These measures may include perimeter fencing around the PV array and other critical facilities, lockable access gates, security lighting, warning and safety signage, anti-theft mounting arrangements, protective enclosures for electrical equipment, and any site-specific security enhancements. The scope shall also include PV module cleaning equipment and any additional protective measures required to ensure the safe, secure, and reliable operation of the installation throughout its service life.

- Earthing (Grounding) and Lightning Protection System: The earthing and lightning protection system comprises grounding electrodes, conductors, bonding connections, surge protection devices, and lightning arrestors installed to protect personnel, electrical equipment, and infrastructure from electrical faults, overvoltages, and lightning strikes. The system provides a safe path for fault and lightning currents to dissipate into the ground, reducing the risk of electric shock, equipment damage, fire hazards, and service interruptions, thereby ensuring the safe and reliable operation of the solar pumping installation.

    - System configuration and operating philosophy

The solar pumping systems shall be designed as modular AC bus-based systems, operating at 400 V, 50 Hz AC, and fully synchronized with the existing diesel generator systems. The design shall enable seamless integration between solar power generation and backup power sources while allowing for straightforward future expansion through the addition of PV generation capacity and associated equipment without major modifications to the existing infrastructure.

No battery energy storage system (BESS) shall be included as part of the solar pumping systems. Battery backup, where required, shall be limited to providing sufficient power for pump start-up and control functions for systems up to 15 kW. Normal pumping operations shall be conducted during daylight hours using solar energy. During periods of inadequate solar irradiance, such as cloudy weather or prolonged non-sunny conditions, the existing or proposed backup diesel generator shall supply the required power to operate the pumps and maintain water production.

    - PV Array Installation Requirements

The photovoltaic (PV) arrays shall be installed at locations designated by the Employer at each project site. The layout and installation of the PV arrays, mounting structures, and associated accessories shall be carefully planned to minimize land use and avoid encroachment on arable or agriculturally productive land. The Contractor shall ensure that access routes, equipment placement, and ancillary works are arranged in a manner that minimizes disruption to existing land use activities while maintaining safe operation and accessibility for maintenance.

# MOTOR PUMP UNITS AND ACCESSORIES

  - SCOPE OF SUPPLY AND WORK

The Contractor shall Supply, install, test, and commission complete solar-powered AC motor-pump units, including submersible pumps for boreholes and deep wells or surface pumps for shallow water sources and booster stations. The units shall include pumps, motors, power cables, non-return valves, fittings, supports, and all necessary accessories for a complete and operational water pumping system. Equipment shall be compatible with solar pump VFDs/controllers and suitable for continuous operation under site conditions.

The scope of works shall include, but not be limited to, the following:

- Supply and delivery of motor-pump units and all associated accessories.

- Supply of all mechanical, hydraulic and electrical components required for complete installation.

- Installation of submersible pumps, including dismantling of existing old pumps where required, lowering of new supplied pumps into the borehole, connection to the rising main, cable support arrangements and all associated fittings.

- Installation of surface-mounted pumps, including foundations, base frames, pump supports, suction and discharge pipework connections and vibration control devices where required.

- Supply and installation of non-return valves, isolation valves, fittings, couplings, flanges, adaptors and connection accessories.

- Supply and installation of motor cables, cable joints, cable supports and protective accessories.

- Mechanical alignment, assembly and connection of pump and motor components.

- Connection of the motor-pump unit to the solar pumping controller/VFD and associated electrical and backup power source system.

- Flushing, testing, performance verification and commissioning of the complete pumping system.

- Rectification of defects identified during testing and commissioning.

- Submission of manufacturer's documentation, performance curves, test certificates, operation and maintenance manuals and warranty certificates.

- Training of Employer-designated personnel in operation, routine inspection and maintenance of the installed equipment.

- All materials and equipment shall be new, unused and of proven quality suitable for continuous operation under the environmental and operating conditions prevailing at the project sites.

  - WATER OUTPUT AND PERFORMANCE REQUIREMENTS

    - General requirement

The motor-pump unit shall be capable of delivering the required water output while operating within the performance envelopes specified in Table 2.1A (Submersible Borehole Pumps) and Table 2.1B (Surface Pumps). The Contractor shall select and provide pump units that achieve the required flow rate and total dynamic head (TDH) corresponding to the site-specific duty conditions determined during detailed design.

The performance ranges presented in the schedules define the minimum acceptable hydraulic operating envelope for each motor rating. The proposed pump shall be capable of operating efficiently, reliably, and continuously at any duty point falling within the applicable flow and head range without excessive vibration, cavitation, overheating, or hydraulic instability.

The Contractor shall demonstrate compliance through certified manufacturer's performance curves showing the relationship between flow, head, efficiency, and power consumption. Where a single pump model does not cover the entire specified performance envelope, multiple hydraulic configurations may be proposed, provided that the combined configurations fully satisfy the required flow and head ranges for the respective motor rating.

The required daily water output for each installation shall be determined by the site-specific demand and operating conditions. The selected pump shall be capable of producing the specified daily water volume within the available solar pumping period while maintaining operation within the manufacturer's recommended performance range. The Contractor shall submit calculations demonstrating that the proposed pump, motor, and solar power system are adequately sized to achieve the required water production under the design conditions.

Compliance with the performance schedule shall be verified during testing and commissioning through measurement of flow rate, total dynamic head, power consumption, and operating efficiency. The installed equipment shall achieve the specified duty point and water output requirements and shall perform in accordance with the submitted certified performance curves.

Acceptance Criterion: The offered motor-pump unit shall be deemed compliant only where the certified performance data confirms that the pump can deliver the required flow and head within the ranges specified in Tables 2.1A or 2.1B and achieve the required daily water output under the project operating conditions.

    - Performance Envelope and Compliance

Motor-pump units shall comply with the specified flow and head ranges for each motor rating. Bidders may offer one or more pump configurations provided that the combined performance curves fully cover the required operating envelope. Pump performance, efficiency, and operating range shall be supported by certified manufacturer data.

    - Multiple Configurations and Guaranteed Duty Points:

Where multiple pump configurations are offered under a single motor rating, they shall be evaluated collectively to verify full coverage of the specified performance envelope. The bidder shall clearly identify the guaranteed duty point(s) for each configuration on the submitted performance curves, showing the corresponding flow, head, efficiency, and power requirements. Compliance shall be based on the combined ability of the proposed configurations to meet the full specified operating range.

Example:

| Required envelope: | 37 kW, 20-50 m³/h @ 160-400 m. |
| --- | --- |
| Bidder offers: | Pump A: 20-35 m³/h @ 250-400 m Pump B: 35-50 m³/h @ 160-300 m |
| Result: | Compliant, because together they cover the entire required envelope. |

    - Site-Specific Pump Selection

Final pump selection shall be based on the site duty point determined from actual site requirement  and system design. The Employer may select any suitable low-, medium-, or high-head configuration within the specified performance envelope.

The Employer shall select the hydraulic configuration that best matches the site-specific duty point determined during detailed design. Payment shall be based on the unit rate submitted for the selected configuration. The bidder shall provide certified performance curves corresponding to each hydraulic configuration offered under the specific motor rating. Where a single pump model covers the entire performance envelope (45-100 m³/h and 160-360 m TDH for submersible pumps), a single rate may be submitted. Otherwise, separate rates shall be provided for each hydraulic configuration necessary to achieve complete coverage of the specified envelope.

    - Submittals

For each pump model offered, bidders shall submit technical data sheets, certified performance curves, efficiency data, motor details, dimensional drawings, materials of construction, and evidence of compatibility with solar-powered AC VFD operation. Where multiple pump configurations are required to meet the specified envelope, performance curves for all configurations shall be provided.

    - Tender Pricing

Bidders shall submit unit rates for each motor-pump rating specified in the Performance Schedule. Where multiple hydraulic configurations are required to cover the prescribed flow and head envelope, separate rates shall be provided for each configuration. Unit rates shall be fully inclusive of supply, delivery, installation, testing, commissioning, training, warranty obligations, accessories, and all works necessary to provide a complete and operational pumping system. The Procuring Entity reserves the right to select any hydraulic configuration within the specified performance envelope based on site-specific duty requirements.

Failure to provide complete performance curves and corresponding prices may result in bid rejection.

Example tender pricing: Item: 75 kW Submersible Solar Pumping Unit

| Item No. | Motor Rating | Configuration | Flow Range (m³/h) | TDH Range (m) | Unit | Unit Rate (USD) |
| --- | --- | --- | --- | --- | --- | --- |
|  | 75 kW | High head | 45-60 | 280-360 |  |  |
|  | 75 kW | Medium head | 60-80 | 220-320 |  |  |
|  | 75 kW | Low head | 80-100 | 160-250 |  |  |

  - INSTALLATION, TESTING AND COMMISSIONING

    - Installation

The Contractor shall supply and carry out the complete installation of the motor-pump unit and all associated mechanical, hydraulic, and electrical components required for a fully operational pumping system. Installation shall include positioning and mounting of equipment, installation of pumps, motors, pipework, valves, fittings, cables, supports, protection devices, and all necessary connections to the solar pumping VFD and power supply system. All works shall be performed in accordance with the manufacturer's instructions, approved drawings, and applicable standards.

    - Testing

Upon completion of installation, the Contractor shall conduct all necessary inspections and tests to verify the safety, functionality, and performance of the pumping system. Testing shall include verification of mechanical and electrical installations, protection devices, control systems, motor operation, pipework integrity, and VFD functionality. Performance tests shall confirm compliance with specified flow, head, power consumption, and operating conditions. Any defects identified during testing shall be corrected and the tests repeated until satisfactory results are achieved.

    - Commissioning

Following successful testing, the Contractor shall commission the complete pumping system and demonstrate its reliable and efficient operation under actual site conditions. Commissioning shall include system start-up, verification of operating and protection functions, confirmation of integration with the solar PV and VFD systems, and adjustment of operating parameters. The Contractor shall demonstrate compliance with the specified hydraulic and performance requirements and complete a trial operation period as directed by the Engineer. Upon successful commissioning, all test reports, O&M manuals, warranties, and training shall be provided prior to final acceptance.

  - SUBMERSIBLE BOREHOLE MOTOR-PUMP SET TECHNICAL SPECIFICATION

    - Pump

- Type: Multi-stage centrifugal borehole pump.

- Hydraulic Design: Radial-flow and/or mixed-flow.

- Installation: Vertical submersible installation.

- Application: Potable water supply.

- Operation: Continuous duty.

- Suitable for operation with solar pumping VFD.

- Capable of operating over the full performance envelope specified in Table 2.1A.

- Stable operation without cavitation, excessive vibration or hydraulic instability.

    - Motor

- Type: Water-filled or oil-filled rewindable submersible motor.

- Voltage: 400V AC (3-Phase).

- Frequency: 50 Hz.

- Duty: Continuous Duty (S1).

- Protection Class: Minimum IP68.

- Insulation Class: Minimum PE2/PA/ Class F.

- Starting: Suitable for VFD operation.

- Equipped with thermal protection.

    - Materials

- Pump Casing	Stainless Steel AISI 304/316

- Shaft; Impellers; Diffusers; Fasteners: Stainless Steel

- Motor Housing	; Cable Guard: Stainless Steel

    - Accessories Included

- Non-return valve; Cable guards; Safety wire/rope; Motor cable Cable splice kit; Lifting eye; Dry-run protection interface Nameplates; Couplings and adaptors.

    - .Performance Requirements

- Pump efficiency shall be manufacturer's high-efficiency design.

- Motor efficiency shall comply with IEC standards.

- Pump shall meet the flow and TDH specified in Table 2.1A.

- Certified performance curves shall be submitted.

- Compatible with variable speed operation by VFD.

  - SURFACE MOTOR-PUMP SET TECHNICAL SPECIFICATION

    - Pump

- Type: Centrifugal surface pump.

- Installation: Horizontal or vertical surface mounted.

- Suitable for water transmission and distribution systems.

- Designed for continuous duty operation.

- Fully compatible with solar pumping VFD.

- Capable of operating within the performance envelope specified in Table 2.1B.

    - Motor

- Type: Three-phase induction motor; Voltage: 400V AC. Frequency: 50Hz.

- Duty Rating: Continuous Duty (S1).

- Protection Class: Minimum IP55.

- Insulation Class: Class F minimum

- VFD compatible; Tropicalized windings.

    - Materials

- Pump Casing:	Cast Iron or Stainless Steel

- Impeller; Shaft; Wear Rings: Stainless Steel or Bronze

- Mechanical Seal: Heavy-duty Mechanical Seal

- Base Frame	Galvanized Steel

- Coupling Guard: Steel

    - Accessories Included

- Base frame; Flexible coupling; Coupling guard; Suction and discharge flanges; Pressure gauges.

- Non-return valve; Isolation valves; Vibration pads; Foundation bolts.

    - Performance Requirements

- Performance shall comply with Table 2.1B.

- Pump shall operate continuously within manufacturer's recommended range.

- NPSHr data shall be provided.

- Certified performance curves shall be submitted.

- Suitable for variable speed operation.

# SOLAR PV AND ELECTRICAL SYSTEM

  - GENERAL

Supply, install, test, and commission a complete Solar PV Generator System for solar water pumping applications, including PV modules, mounting structures, foundations, DC cabling, connectors, combiner boxes (where applicable), DC isolators, earthing and lightning protection systems, monitoring components, and all associated accessories required for a complete and operational installation.

The PV array shall comprise high-efficiency monocrystalline or bifacial monocrystalline N-Type TOPCon modules with a minimum module rating of 650 Wp, IEC 61215 and IEC 61730 certified, suitable for 1500 VDC operation, and installed on corrosion-resistant support structures.

The PV array shall be sized in accordance with the pump motor rating and system requirements, with a total installed PV capacity not less than 1.75 times and not greater than 2.0 times the rated motor power unless otherwise approved by the Engineer. The array configuration shall be optimized to operate within the voltage and current limits of the solar pumping VFD/controller while maximizing annual energy production and minimizing shading and mismatch losses.

The Contractor shall provide manufacturer's technical data sheets, certificates of conformity, factory test reports, warranty certificates, and as-built documentation for all supplied equipment.

  - MODULE SPECIFICATIONS

All PV modules shall be supplied with Certificates of Origin, Factory Test Certificates, and Quality Certificates. The modules shall comply with the following minimum requirements:

    - Bifacial Solar PV Module Minimum Technical Requirements:

| Module Type | Bifacial Monocrystalline PV Module |
| --- | --- |
| Cell Technology | N-Type Topco or equivalent |
| Rated Maximum Power (Pmax) | ≥ 550 Wp |
| Module Efficiency | ≥ 21% |
| Bifaciality Factor | ≥ 80% |
| Module Construction | Glass-Glass |
| Front/Rear Glass | Tempered glass, minimum 2.0 mm thick |
| Cell Configuration | 132-144 half-cut cells |
| Maximum System Voltage | 1500 VDC |
| Power Tolerance | 0 to +5 W |
| Operating Temperature Range | -40°C to +85°C |
| Junction Box Protection | IP68 minimum |
| Connectors | MC4 compatible or equivalent |
| Wind Load Resistance | ≥ 2400 Pa |
| Snow Load Resistance | ≥ 5400 Pa |
| Degradation Rate | ≤ 1% in first year and ≤ 0.40% annually thereafter |
| Product Warranty | Minimum 12 years |
| Performance Warranty | Minimum 30 years |
| Standards | IEC 61215 and IEC 61730 |
| Quality Management Certifications | ISO 9001, ISO 14001, and ISO 45001 |
| Identification | Permanent nameplate with unique serial number traceability |

Note: All PV modules shall be factory tested, supplied with manufacturer's technical data sheets, warranty certificates, certificates of conformity, and country of origin documentation. Modules shall be new, unused, and sourced from a recognized manufacturer with proven field performance.

    - Monocrystalline Solar PV Module

The photovoltaic modules shall be high-efficiency monocrystalline N-Type TOPCon technology with a minimum rated output of 650 Wp per module, minimum module efficiency of 22%, IEC 61215 and IEC 61730 certified, suitable for operation at 1500 VDC, and supplied with a minimum 12-year product warranty and 25-year linear performance warranty.

Minimum Technical Requirements

| Parameter | Requirement |
| --- | --- |
| Module Type | Monocrystalline Silicon Solar PV Module |
| Cell Technology | Mono PERC, N-Type TOPCon, or equivalent technology |
| Rated Maximum Power (Pmax) | ≥ 650 Wp |
| Module Efficiency | ≥ 22% |
| Power Tolerance | 0 to +5 W or better |
| Front Glass | High-transmission tempered low-iron glass |
| Back sheet / Rear Glass | Weather-resistant multilayer backsheet |
| Frame | Anodized corrosion-resistant aluminum alloy |
| Junction Box | IP68 minimum |
| Connectors | MC4 compatible or equivalent |
| Maximum System Voltage | 1500 VDC |
| Operating Temperature | -40°C to +85°C |
| Wind Load Resistance | Minimum 2400 Pa |
| Snow Load Resistance | Minimum 5400 Pa |
| Fire Safety Rating | Class C or better |
| Module Degradation | ≤ 2% in first year and ≤ 0.55% annually thereafter |
| Product Warranty | Minimum 12 years |
| Performance Warranty | Minimum 25 years |
| Standards Compliance | IEC 61215 and IEC 61730 |
| Quality Certifications | ISO 9001, ISO 14001, ISO 45001 |
| Marking | Permanent nameplate, serial number, and traceability identification |

Documentation Requirements

The Contractor shall submit:

- Manufacturer's technical datasheets.

- IEC compliance certificates.

- Factory quality certificates.

- Flash-test reports.

- Product and performance warranty certificates.

- Mechanical load test certificates.

- Module installation, operation, and maintenance manuals.

  - PV COMBINER BOXES AND DC ELECTRICAL

    - General

The Contractor shall supply, install, test, and commission photovoltaic (PV) combiner boxes and associated DC electrical protection equipment for the solar pumping systems.

PV combiner boxes shall be provided for PV arrays comprising three (3) or more strings and shall combine multiple PV strings into a common DC output for connection to the solar pumping inverter/VFD. The combiner boxes shall incorporate all protection, isolation, monitoring, and termination components necessary for safe and reliable operation.

The combiner boxes shall be designed for outdoor installation under harsh environmental conditions and shall provide adequate protection against overcurrent, reverse current, overvoltage, lightning surges, moisture, dust, and unauthorized access.

Where the number of PV strings exceeds twenty-four (24), multiple combiner boxes shall be provided and distributed to ensure safe operation, maintainability, and cable management.

Example Configuration

| Total PV Strings | Acceptable Arrangement |
| --- | --- |
| 30 | 2 × 15-string combiner boxes |
| 36 | 2 × 18-string combiner boxes |
| 44 | 2 × 22-string combiner boxes |

    - Minimum Technical Requirements

| Parameter | Minimum Requirement |
| --- | --- |
| Enclosure Material | Powder-coated stainless steel, galvanized steel, or GRP |
| Degree of Protection | IP65 minimum |
| Installation | Outdoor |
| System Voltage | 1000 VDC or 1500 VDC to match PV array design |
| Input Capacity | Required number of strings + minimum 2 spare inputs |
| String Fuse Rating | Minimum 1.25 × String Isc |
| Main DC Isolator | Minimum 1.25 × Total Array Current |
| Surge Protection | Type I or Type II DC SPD |
| Reverse Current Protection | Required |
| Busbars | Tinned Copper |
| Ambient Temperature | -30°C to +70°C |
| Warranty | Minimum 2 Years |

    - Integrated Components

Each combiner box shall be complete with the following integrated components:

Enclosure

- Corrosion-resistant IP65 outdoor enclosure.

- Powder-coated stainless steel, galvanized steel, or GRP construction.

- Lockable access door.

- Internal DIN rail arrangement.

- Adequate ventilation where required.

- Suitable cable entry and termination space.

PV String Fuses

- Individual fuse protection for each PV string.

- PV-rated gPV cartridge fuses.

- Fuse rating not less than 125% of string short-circuit current (Isc).

- DIN rail mounted fuse holders.

DC Isolator Switch

- Load-break DC isolator. Rated for full array voltage and current. Minimum 1000 VDC. Breaking capacity suitable for solar PV applications. Lockable in OFF position.

DC Circuit Breaker (Where Required)

- PV-rated DC breaker. Current rating sized for combined array current. Minimum 125% of maximum continuous operating current.

Surge Protection Devices (SPD):

- Type I or Type II DC SPD as required by site lightning risk assessment.

- Installed between: Positive (+) and Earth; Negative (-) and Earth

- Replaceable plug-in modules. Visual status indication. Minimum discharge current: In ≥ 20 kA (8/20 µs)

DC Busbars

- Tinned copper busbars. Sized for combined string current with minimum 25% safety margin.

- Designed for continuous operation under maximum current conditions.

String Inputs and Connectors

- UV-resistant PV cable terminations. MC4-compatible connectors. Individual identification for each string. Suitable for system voltage and current.

Cable Glands and Terminations

- IP68 UV-resistant cable glands. Appropriate compression lugs and cable termination accessories. Proper strain relief arrangements.

Earthing and Bonding

- Dedicated earth bar. Earthing terminals for all metallic components. Equipotential bonding of enclosure, SPDs, mounting structures, and associated electrical equipment.

- Connection to the solar plant earthing system.

Labels and Warning Notices

Provide durable UV-resistant labels indicating:

- Combiner Box Identification Number; String Numbers; DC Voltage; DC Current Rating; Danger High Voltage Warning; Isolation Instructions; SPD Status Identification; Earthing Identification

    - Testing and Commissioning

The Contractor shall perform the following tests before commissioning:

- Visual and mechanical inspection; Verification of fuse ratings. Verification of SPD installation and operation.

- Continuity testing. Insulation resistance testing. Verification of polarity. Verification of earthing continuity.

- Functional testing of DC isolators and breakers.

- Verification of string current measurements.

- Verification of DC voltage at combiner box output.

Test records shall be submitted as part of the commissioning documentation.

  - SOLAR PUMP INVERTERS/ CONTROLLER (HYBRID SOLAR PUMPING SYSTEM)

    - General

Supply, install, test, and commission solar pump inverter/controllers for solar-powered water pumping systems with provision for hybrid operation with diesel generators and/or utility grid backup. The inverter shall incorporate MPPT, Variable Frequency Drive (VFD), data logging, and intelligent power management functions. The inverter rating shall be a minimum of one standard size above the connected motor load or not less than 125% of the motor rated power.

    - Minimum Technical Requirements

| Application | Solar water pumping, hybrid operation |
| --- | --- |
| Capacity Range | 1.5 kW to 350 kW |
| Inverter Sizing | ≥125% of pump motor rating or next higher standard size |
| Output Voltage | 380/415 VAC |
| Output Phase | Three-phase |
| Frequency | 50 Hz |
| Efficiency | ≥95% |
| Protection Rating | IP55 minimum |
| Maximum DC Input Voltage | ≥1000 VDC |
| Operating Temperature | Up to +45°C |
| MPPT | Integrated |
| VFD Function | Integrated |
| Monitoring & Data Logging | Integrated |

    - Functional Requirements

The inverter/controller shall provide:

- Automatic MPPT tracking.

- Soft-start and speed control of pump motors.

- Stable operation during solar irradiance fluctuations.

- Automatic start/stop functions.

- Hybrid operation with solar, generator, and/or grid power.

- Water level monitoring and control.

- Dry-run and tank-full protection.

- Fault diagnostics and event logging.

    - Monitoring and Protection

The inverter shall include a local display and monitoring functions for PV voltage, current, power, AC output, motor current, frequency, operating status, and energy production. Minimum protections shall include reverse polarity, overvoltage, overload, overcurrent, short circuit, overtemperature, phase loss, phase imbalance, ground fault, dry running, and low solar input power.

    - Documentation

The Contractor shall submit manufacturer data sheets, operation manuals, test certificates, warranty documentation, and evidence of compatibility with solar-powered water pumping applications.

# SYSTEM AC/DC CABLES AND ACCESSORIES

  - GENERAL REQUIRMENT

The Contractor shall supply, install, test, and commission all AC and DC cables, cable terminations, connectors, glands, conduits, trays, trenching systems, and associated accessories required for the complete and reliable operation of the solar pumping system.

All cables shall be new, of approved manufacture, suitable for the intended application, and compliant with the latest editions of applicable standards, including:

- IEC 60364-5-52: Selection and erection of electrical equipment - Wiring systems

- IEC 62548: Photovoltaic (PV) Arrays - Design Requirements

- IEC 60228: Conductors of Insulated Cables

- IEC 60502 (where applicable)

Cable sizing shall be based on:

- Continuous operating current.

- Ambient temperature conditions.

- Installation method.

- Grouping factors.

- Future expansion requirements.

- Voltage drop limitations.

The Contractor shall submit cable sizing calculations and voltage drop calculations for review and approval.

Maximum Permissible Voltage Drop

- DC Circuits: Maximum 2%

- AC Circuits: Maximum 3%

Unless otherwise justified by design calculations, cables shall be rated for not less than 125% of the maximum continuous operating current.

  - AC POWER CABLES

AC power cables shall be copper conductor XLPE insulated cables suitable for the installation conditions. Underground and direct-buried cables shall be steel wire armored (SWA) or equivalent armored type. Above-ground cables installed in cable trays, conduits, or control panels may be unarmored where adequate mechanical protection is provided.

- Underground installations: CU/XLPE/SWA/PVC (Steel Wire Armoured) or equivalent armored cable.

- Direct burial installations: Armored cable mandatory.

- Cable trays, conduits, and indoor installations: Unarmored XLPE/PVC cable may be accepted where adequate mechanical protection is provided.

AC power cables shall be used for connections between the inverter/VFD, control panels, backup power systems, motors, and associated AC equipment.

Minimum Technical Requirements

| Cable Type | CU/XLPE/PVC/SWA/PVC or equivalent armored cable |
| --- | --- |
| Conductor Material | Stranded Copper |
| Conductor Class | Class 2 or Class 5 |
| Number of Cores | As required by the system design |
| Size Range | 2.5 mm² to 300 mm² |
| Voltage Rating | 0.6/1 kV |
| Insulation | XLPE |
| Sheath | PVC, UV-resistant |
| Armour | Steel Wire Armour (SWA) where required |
| Installation | Above ground, underground, outdoor and direct burial applications |
| Standard | IEC 60502 |

All cables exposed to outdoor conditions shall be UV resistant and suitable for high-temperature environments.

  - DC SOLAR PV CABLES

DC string and feeder cables shall be solar PV-rated, double-insulated, UV-resistant XLPO cables. Armoring shall not be required unless specifically identified by the design or site conditions, in which case the cables shall be installed in protective conduits or armored cable systems.

    - DC string cables: shall be used for interconnection of PV modules and connection of PV strings to combiner boxes.

Minimum Technical Requirements

| Cable Type | Solar PV Cable |
| --- | --- |
| Standard | EN 50618 / IEC 62930 |
| Conductor Material | Tinned Stranded Copper |
| Conductor Size | Minimum 6 mm² |
| Voltage Rating | Minimum 1000 VDC (1500 VDC preferred) |
| Insulation | XLPO |
| Outer Sheath | XLPO |
| Construction | Double Insulated |
| UV Resistance | Required |
| Ozone Resistance | Required |
| Flame Retardant | Required |
| Halogen-Free | Required |
| Operating Temperature | -40°C to +90°C |
| Certification | TÜV or Equivalent |

All DC cables shall be tested for continuity, polarity, and insulation resistance prior to commissioning.

    - DC Main Feeder Cables: DC feeder cables shall connect PV combiner boxes to the solar inverter or solar pumping VFD.

Minimum Technical Requirements

| Cable Type | Solar PV DC Feeder Cable |
| --- | --- |
| Conductor Material | Tinned Copper |
| Conductor Size | 6 mm² to 300 mm² |
| Voltage Rating | Minimum 1000 VDC (1500 VDC where applicable) |
| Insulation | Double Insulated XLPO |
| UV Resistance | Required |
| Flame Retardant | Required |
| Halogen-Free | Required |
| Certification | TÜV or Equivalent |
| Maximum Voltage Drop | ≤ 2% |

Cable sizes shall be determined by approved design calculations to ensure compliance with current carrying capacity and voltage drop requirements.

  - WATER LEVEL SENSOR AND CONTROL CABLES

Water level sensor cables shall be provided for borehole level monitoring, storage tank level control, dry-run protection, and automatic pump operation.

Minimum Technical Requirements

| Cable Type | Water Level Sensor Cable |
| --- | --- |
| Number of Conductors | 2 Core Minimum |
| Conductor Size | Minimum 1.5 mm² |
| Probe Material | Stainless Steel |
| Probe Insulation | Polyurethane |
| Cable Jacket | PVC or Polyurethane |
| UV Resistance | Required |
| Flame Retardant | Required |
| Construction | Double Insulated |
| Service Condition | Suitable for Continuous Immersion |
| Application | Borehole and Tank Level Monitoring |

  - CABLE CONTAINMENT SYSTEMS

    - Cable Trays

The Contractor shall supply, install, test, and commission cable tray systems complete with supports, fixings, covers, and accessories.

All above-ground power and control cables shall be routed within cable trays or approved cable support systems.

Minimum Technical Requirements

| Material | Hot-Dip Galvanized Steel |
| --- | --- |
| Galvanizing Thickness | Minimum 120 Microns |
| Tray Thickness | Minimum 1.2 mm |
| Tray Width | Minimum 200 mm |
| Tray Depth | Minimum 100 mm |
| Cover | Removable Galvanized Cover |
| Finish | Hot-Dip Galvanized or Powder Coated |
| Installation | Indoor and Outdoor |
| Spare Capacity | Minimum 25% |

Accessories

The cable tray system shall include:

- Tray supports; Wall brackets; Base supports; Covers; Couplers; Bends and tees; Reducers; Fasteners; Cable cleats; Cable ties; Identification labels

- Cable trays shall be securely fixed to structures and adequately supported to prevent excessive deflection.

    - Cable Trenches and Underground Ducting

The Contractor shall construct cable trenches and provide underground cable duct systems where required. All underground cable installations shall provide adequate mechanical protection, drainage, accessibility, and future cable expansion provisions.

Minimum Technical Requirements

| Minimum Trench Depth | 600 mm |
| --- | --- |
| Duct Material | PVC Schedule 40 or HDPE |
| Duct Accessories | Elbows, Tees, Couplings and Adaptors |
| Pull Rope | 12 mm Nylon Rope |
| Bedding Layer | Minimum 100 mm Sand Bedding |
| Backfilling | Selected Granular Material |
| Marker Tape | Yellow or Orange Warning Tape |
| Cable Protection | Ducted Installation |
| Access Points | Pull Boxes and Manholes Where Required |

  - INSTALLATION REQUIREMENTS

- Underground cables shall be installed inside protective conduits.

- A minimum 100 mm sand bedding shall be provided below and above the conduits.

- Warning tape shall be installed not less than 300 mm above the cable route.

- Pull pits or manholes shall be installed at changes of direction and at intervals necessary for cable pulling.

- All exposed ducting and accessories shall be UV-resistant and suitable for outdoor use.

- Cable routes shall be clearly marked and recorded on as-built drawings.

  - TESTING

Upon completion, the Contractor shall carry out:

- Continuity testing.

- Insulation resistance testing.

- Verification of cable identification.

- Verification of phase sequence (AC circuits).

- Verification of polarity (DC circuits).

- Inspection of cable containment systems.

All test results shall be submitted as part of the commissioning documentation.

# BACKUP POWER SUPPLY SOURCE SYSTEM

  - GENERAL

The Contractor shall be responsible for the, supply, delivery, installation, testing, commissioning, training, warranty, and after-sales support of a complete Backup Power Supply System for water pumping facilities.

The system shall provide reliable power to all designated pump loads and associated control equipment during utility power interruptions and shall comprise one or a combination of the following:

- Diesel Generator Set (Genset)

- Grid Interconnection Equipment

- Battery Energy Storage System (BESS)

- Hybrid Inverter System

- Automatic/ Manual Transfer Switch (ATS/MTS)

- Protection and Control Systems

- All associated cabling, accessories, civil works, and installation materials

The Contractor shall verify site conditions and electrical loads before procurement and installation.

Any component not specifically mentioned but necessary for safe, complete, and reliable operation shall be deemed included in the Contractor's scope.

  - DIESEL GENERATOR SET

    - General

The Contractor shall supply, deliver, install, test, commission, and place into operation a complete Diesel Generator Set, canopy type, 45 kVA (Primary rated Power), 4-stroke diesel engine, 3-phase, 400 V, 50 Hz, 1500 rpm, complete and factory-assembled; including control panel, AVR, starter batteries, battery charger, auxiliary cabling, exhaust system with silencer, fuel supply and return piping, cooling system, and all accessories. The generator shall be mounted on a common base frame with integrated base fuel tank sized for minimum 8 hours continuous operation at full load, fitted with anti-vibration mounts, and enclosed in a weatherproof acoustic canopy providing noise attenuation to maximum 75 dBA at 1 m. Rated for site conditions of 30°C ambient temperature and elevation 2555 m a.s.l., complete with installation, testing, and commissioning.

The generator set shall be a factory-assembled diesel-engine-driven AC generating set suitable for standby operation and capable of supplying all specified loads including pump motor starting currents.

The standby generator capacity shall include not less than 20% spare capacity above the maximum calculated demand.

    - Technical Specifications

A. Generator Set

| Type | Diesel Engine Driven Generator Set |
| --- | --- |
| Duty | Standby Operation |
| Capacity | Minimum 120% of Maximum Connected Load |
| Output Voltage | 400/220 VAC |
| Phase | 3-Phase |
| Frequency | 50 Hz |
| Power Factor | 0.8 |
| Voltage Regulation | ±1% |
| Frequency Regulation | ±1% |
| Total Harmonic Distortion | ≤ 5% |
| Starting System | 24 VDC Electric Start |

B. Engine

| Type | Four-Stroke Diesel Engine |
| --- | --- |
| Cooling System | Water-Cooled |
| Fuel System | Direct Injection |
| Aspiration | Naturally Aspirated or Turbocharged |
| Duty Rating | Heavy-Duty Industrial |
| Approved Manufacturers | Cummins, Perkins, Volvo Penta, MTU, Caterpillar, or Approved Equivalent |

C. Alternator

| Type | Brushless |
| --- | --- |
| Excitation | Self-Excited with AVR |
| PMG Excitation | Preferred |
| Insulation Class | Class H |
| Temperature Rise | Class B |
| Protection Class | IP23 Minimum |
| Voltage Stability | ±1% |

D. Control Panel

The generator controller shall provide:

| Functions | - Automatic Start/Stop; Manual Start/Stop; Remote Start Capability; Event Logging; Automatic Fault Shutdown |
| --- | --- |
| Measurements | - Voltage; Current; Frequency; Kw; kVA; Power Factor; Running Hours; Oil Pressure; Coolant Temperature; Battery Voltage |
| Protection Functions | - Low Oil Pressure; High Coolant Temperature; Overspeed; Underspeed; Overvoltage; Undervoltage; Overcurrent; Short Circuit; Overcrank; Emergency Stop |

E. Fuel System

| Fuel Tank | Base Tank or Separate Day Tank |
| --- | --- |
| Fuel Autonomy | Minimum 24 Hours at 75% Load |
| Fuel Gauge | Required |
| Drain Valve | Required |
| Spill Containment | Required |
| Flexible Connections | Required |

F. Acoustic Enclosure

| Construction | Weatherproof, Powder-Coated Steel |
| --- | --- |
| Corrosion Protection | Required |
| Access Doors | Lockable |
| Sound Attenuation | Integrated |
| Noise Level | ≤ 75 dBA at 1 m |

G. Foundation Works

The Contractor shall design and construct a reinforced concrete foundation complete with excavation, filling, compaction, and reinstatement works.

| Concrete Grade | C25 Minimum |
| --- | --- |
| Reinforcement Strength | 420 MPa |
| Rebar Diameter | 12 mm Minimum |
| Foundation Height | Minimum 300 mm Above Ground |
| Foundation Projection | Minimum 250 mm Beyond Enclosure |
| Vibration Isolation | Anti-Vibration Mounts Required |

    - Installation, Testing and Commissioning

Installation

Install the generator set, foundation, fuel system, exhaust system, batteries, control wiring, power cabling, earthing, and all associated accessories in accordance with manufacturer's recommendations and approved drawings.

Testing

Testing shall include:

- Factory Acceptance Testing (FAT)

- Load bank testing at 25%, 50%, 75%, and 100% load

- Verification of protection functions and alarms

- Battery and starting system tests

- Automatic start/stop and transfer sequence verification

Commissioning

Commission the complete system and demonstrate satisfactory operation under site conditions. Provide operator training and submit all manuals, test reports, certificates, and as-built drawings prior to handover.

  - BATTERY ENERGY STORAGE SYSTEM (BESS)

    - General scope of supply and works

The Contractor shall supply, deliver, install, test, commission, and place into operation a complete Battery Energy Storage System (BESS) for hybrid solar power applications. The system shall include battery modules, battery racks, battery management system (BMS), hybrid inverter/charger, monitoring and control systems, protection equipment, electrical interconnections, enclosures, ventilation systems, foundations, earthing, and all associated accessories required for a fully functional and safe energy storage system.

The BESS shall be suitable for integration with solar PV systems, diesel generators, utility grid connections, and critical AC loads, and shall provide energy storage, load management, backup power, and system stabilization functions.

The battery backup system shall include all batteries, battery racks/cabinets, BMS, hybrid inverter/controller, DC protections, battery monitoring equipment, communication interfaces, battery interconnection cables, busbars, installation materials, testing, commissioning, training, documentation, and warranty necessary for a complete operational system. Battery autonomy and system sizing shall be as specified in the technical specifications. Solar PV equipment shall be measured and paid for separately.

Technical Specifications

A. Battery System

| Battery Technology | Lithium Iron Phosphate (LiFePO4) |
| --- | --- |
| Battery Configuration | Modular and Scalable |
| Nominal System Voltage | As per manufacturer's design |
| Usable Capacity | As specified in project requirements |
| Depth of Discharge (DoD) | ≥ 90% |
| Round Trip Efficiency | ≥ 90% |
| Design Life | Minimum 15 Years |
| Cycle Life | Minimum 6,000 Cycles at 80% DoD |
| Operating Temperature | -10°C to +50°C |
| Protection Rating | Minimum IP54 (Indoor), IP55 (Outdoor) |
| Battery Management System (BMS) | Integrated |

B. Battery Management System (BMS)

The Battery Management System shall provide:

- Cell voltage monitoring.

- Battery temperature monitoring.

- State of Charge (SOC) monitoring.

- State of Health (SOH) monitoring.

- Cell balancing.

- Overcharge protection.

- Deep discharge protection.

- Short-circuit protection.

- Overcurrent protection.

- Fault alarms and event logging.

- Communication with inverter and monitoring system.

C. Battery Racks and Enclosures

| Rack Type | Modular Steel Rack System |
| --- | --- |
| Construction | Powder-Coated Galvanized Steel |
| Corrosion Protection | Required |
| Seismic Stability | Required |
| Access | Front Access for Maintenance |
| Ventilation | Natural or Forced Ventilation |
| Cable Management | Integrated |
| Expansion Capability | Minimum 25% Spare Capacity |

D. Hybrid Inverter / Battery Converter

| Type | Bi-Directional Hybrid Inverter |
| --- | --- |
| Application | Solar PV, Battery, Generator and Grid Integration |
| Rated Power | As Project Requirement |
| Output Voltage | 400/230 VAC |
| Output Phase | Three Phase |
| Frequency | 50 Hz |
| Efficiency | ≥ 96% |
| Protection Rating | IP55 Minimum |
| PV Integration | Compatible |
| Generator Integration | Compatible |
| Grid Integration | Compatible |
| Battery Integration | Compatible |
| Parallel Operation | Supported |
| Monitoring | Integrated |
| Functional Features | - Battery charging and discharging. - Automatic energy management. - Peak shaving and load shifting. - Generator support. - Black-start capability. - Grid synchronization where applicable. - Automatic source selection. - Remote monitoring and diagnostics. |

E. Protection Systems

The BESS shall include: DC isolators.; DC circuit breakers.; AC circuit breakers. Surge protection devices (AC and DC). Earthing and bonding system. Fire detection system. Emergency shutdown system. Reverse polarity protection. Ground fault protection. Thermal protection.

F. Monitoring and Control

The BESS shall provide: Local HMI display. Battery status monitoring. Charge/discharge monitoring. Energy flow monitoring. Historical data logging. Fault and alarm reporting. Ethernet/RS485 communication. Remote monitoring capability.

    - Installation, Testing and Commissioning

The Contractor shall:

Installation

- Install battery modules, racks, inverter, protection systems, cabling, and monitoring equipment.

- Complete all electrical, civil, earthing, and communication works.

- Provide all labels, warning signs, and safety equipment.

Testing

- Insulation resistance testing. Battery capacity verification. Charge/discharge testing. Protection function testing. Communication testing. System integration testing. Functional operation testing.

Commissioning

- Demonstrate safe and reliable operation. Verify charging and discharging functions. Verify integration with PV, generator, and grid systems. Conduct performance and autonomy testing. Provide operator training and handover documentation.

    - BATTERY HYBRIDE SYSTEM COMPLIANCE SCHEDULE

| Parameter | Requirement | Comply (Yes/No) | Offered Specification |
| --- | --- | --- | --- |
| Battery Technology | LiFePO4 |  |  |
| Modular Design | Required |  |  |
| Integrated BMS | Required |  |  |
| DoD ≥ 90% | Required |  |  |
| Cycle Life ≥ 6,000 Cycles | Required |  |  |
| Design Life ≥ 15 Years | Required |  |  |
| Round Trip Efficiency ≥ 90% | Required |  |  |
| Hybrid Inverter Included | Required |  |  |
| Three-Phase Output | Required |  |  |
| Generator Integration | Required |  |  |
| Grid Integration | Required |  |  |
| Solar PV Integration | Required |  |  |
| Remote Monitoring | Required |  |  |
| DC Protection Devices | Required |  |  |
| AC Protection Devices | Required |  |  |
| Surge Protection | Required |  |  |
| Fire Detection System | Required |  |  |
| Emergency Shutdown | Required |  |  |
| Earthing System | Required |  |  |
| Factory Tested | Required |  |  |
| Installation Included | Required |  |  |
| Testing & Commissioning Included | Required |  |  |
| O&M Manuals Provided | Required |  |  |
| Training Included | Required |  |  |
| Warranty Provided | Required |  |  |

Manufacturer Information

| Item | Offered |
| --- | --- |
| Battery Manufacturer |  |
| Battery Model |  |
| Battery Chemistry |  |
| Usable Capacity (kWh) |  |
| Nominal Voltage (V) |  |
| Hybrid Inverter Manufacturer |  |
| Hybrid Inverter Model |  |
| Inverter Rating (kW) |  |
| Battery Cycle Life |  |
| Product Warranty (Years) |  |
| Performance Warranty (Years) |  |

  - GRID INTERCONNECTION SYSTEM

    - General

The Contractor shall design, supply, deliver, install, test, commission, and obtain utility approval for a complete grid interconnection system for solar-powered water supply and pumping facilities.

The grid connection arrangement shall be selected based on utility requirements and available network infrastructure and may comprise either:

Option 1 :Low Voltage (LV) Direct Grid Connection

Direct connection to the existing 400/220V, 50 Hz utility distribution network through a dedicated LV interconnection panel.

Option 2: Transformer-Based MV/HV Grid Connection

Connection to the utility network through a dedicated distribution transformer and associated MV/HV interconnection facilities.

The Contractor shall provide all equipment, cabling, protection systems, metering, earthing, accessories, approvals, testing, and ancillary works necessary for a complete operational system, whether specifically mentioned or not.

    - Applicable Standards

All equipment and installation works shall comply with the latest editions of:

- IEC 60364 - Electrical Installations

- IEC 61439 - Low Voltage Switchgear Assemblies

- IEC 60947 - Low Voltage Switchgear and Controlgear

- IEC 60076 - Power Transformers

- IEC 62271 - Medium Voltage Switchgear

- IEC 60255 - Protection Relays

- IEC 60529 - Enclosure Protection Ratings

- IEC 62305 - Lightning Protection

- Applicable Utility Grid Codes

- Applicable National Electrical Codes

    - Low Voltage (LV) Direct Grid Connection

- Scope

The LV Grid Connection System shall provide a direct interface between the utility low-voltage network and the pumping facility.

The scope shall include:

- LV interconnection panel

- Incoming and outgoing MCCBs

- Utility isolation switch

- Revenue-grade utility metering

- Surge protection devices (SPD)

- Protection devices

- Control and power wiring

- Cable terminations

- Earthing and bonding system

- Testing and commissioning

- Utility coordination and approvals

- Minimum Technical Requirements

| System Voltage | 400/230 VAC |
| --- | --- |
| Frequency | 50 Hz |
| System Type | Three Phase, Four Wire |
| Enclosure | Indoor IP54 / Outdoor IP65 |
| Busbars | Copper |
| Metering | Utility-approved revenue-grade meter |
| Protection | MCCBs, Earth Fault and SPD |
| Earthing | Complete earthing and bonding system |

    - Transformer-Based MV/HV Grid Connection

- Scope

The transformer-based grid connection system shall provide complete interconnection between the utility MV/HV network and the facility LV distribution system.

The scope shall include:

- Distribution transformer; MV switchgear (RMU/LBS/Circuit Breaker); LV switchgear Metering equipment Protection relays Surge arresters Earthing system Transformer accessories Protection and control wiring Transformer foundation (where specified) Testing and commissioning Utility approvals

- Distribution Transformer Requirements

| Type | Oil-Filled ONAN or Dry-Type |
| --- | --- |
| Installation | Outdoor |
| Rating | As Per Design |
| Voltage Ratio | 15/0.4 kV or 33/0.4 kV |
| Frequency | 50 Hz |
| Vector Group | Dyn11 |
| Standard | IEC 60076 |
| Accessories | Surge Arresters, Earthing and Protection Devices |

- Medium Voltage Switchgear

Provide:

- Ring Main Unit (RMU) or Load Break Switch (LBS)

- Circuit Breaker (where required)

- Earthing Switch

- Surge Arresters

- Metering Compartment

- Protection Devices

- Low Voltage Switchgear

Provide:

- Main Incomer Breaker

- Copper Busbar System

- MCCBs

- Surge Protection Devices

- Protection Relays

- Metering Instruments

- Protection Relays

Numerical relays shall include:

- Overvoltage (ANSI 59)

- Undervoltage (ANSI 27)

- Overfrequency (ANSI 81O)

- Underfrequency (ANSI 81U)

- Overcurrent (ANSI 50/51)

- Earth Fault (ANSI 50N/51N)

- Reverse Power (ANSI 32)

    - Testing and Commissioning

The Contractor shall carry out factory and site testing, including:

- Transformer routine tests; Switchgear testing; Relay testing and settings verification; Meter calibration verification; Insulation resistance testing; Earth resistance testing; CT/VT testing; Transformer ratio testing; Functional and interlocking tests; Utility witness testing

    - Documentation

The Contractor shall submit:

- Single Line Diagrams (SLD); Equipment Datasheets; Factory Test Reports; Transformer Test Certificates; Meter Calibration Certificates; Protection Settings Reports; Site Test Reports; Utility Approval Documents; O&M Manuals; As-Built Drawings

    - Warranty

All equipment and installation works shall be covered by a minimum 24-month warranty from the date of commissioning. The Contractor shall repair or replace defective equipment at no additional cost to the Employer.

    - Grid Interconnection System Compliance Schedule

| Parameter | Requirement | Comply (Yes/No) | Offered Specification |
| --- | --- | --- | --- |
| Complete Grid Connection System | Required |  |  |
| Utility Approval Included | Required |  |  |
| IEC-Compliant Equipment | Required |  |  |
| LV Direct Connection Option Available | Yes, Where Applicable |  |  |
| MV/HV Transformer Connection Option Available | Yes, Where Applicable |  |  |
| Utility Revenue Metering | Required |  |  |
| Earthing System | Required |  |  |
| Surge Protection | Required |  |  |
| Protection Relays | Required |  |  |
| Testing & Commissioning Included | Required |  |  |
| O&M Manuals Included | Required |  |  |
| Warranty ≥ 24 Months | Required |  |  |

    - Transformer-Based Connection (Where Applicable)

| Parameter | Requirement | Offered |
| --- | --- | --- |
| Transformer Manufacturer | State |  |
| Transformer Rating (kVA) | State |  |
| Voltage Ratio | 15/0.4 kV or 33/0.4 kV |  |
| Transformer Type | Oil-Filled or Dry Type |  |
| Vector Group | Dyn11 |  |
| RMU/LBS Manufacturer | State |  |
| Protection Relay Manufacturer | State |  |
| Utility Meter Type | State |  |

Tender Note

Grid interconnection rates shall include all equipment, installation, testing, commissioning, utility coordination, and approvals within the project boundary. Utility network extensions, utility poles, overhead lines, right-of-way acquisition, and utility infrastructure outside the project boundary shall be excluded unless specifically identified in the call-off contract.

# MAIN DISTRIBUTION PANELS AND CONTROL SYSTEM

  - MAIN DISTRIBUTION BOARD

    - Scope of Works

The Contractor shall supply, install, test, commission, and place into operation complete Main Distribution Panels (MDPs) and Control Systems for solar-powered water pumping installations. The works shall include all switchgear, protection devices, control equipment, monitoring components, cabling terminations, interconnections, labeling, testing, and accessories required for safe, reliable, and automatic operation of the pumping system.

The system shall provide power distribution, motor control, monitoring, protection, automatic operation, and interface with solar pump inverters, generators, utility power supply (where applicable), water level sensors, and pump equipment.

    - Minimum Technical Specification

| Panel Type | Main Distribution Panel (MDP) and Control Panel |
| --- | --- |
| Construction | Powder-coated steel cabinet, floor or wall mounted |
| Protection Rating | IP54 indoor, IP65 outdoor minimum |
| Nominal Voltage | 380/415 VAC |
| Frequency | 50 Hz |
| System Phase | Three-phase, four-wire |
| Busbar Material | Copper, adequately rated |
| Control Voltage | 24 VDC or manufacturer standard |
| Cable Entry | Top or bottom gland plate |
| Metering | Digital multifunction energy meter |
| HMI/Display | Local display for system status and alarms |
| Generator Interface | Provision for generator integration |
| Solar Inverter Interface | Compatible with solar pump VFD/inverter |
| Enclosure Finish | Corrosion-resistant, suitable for outdoor environments |
| Identification | Permanent labels and engraved nameplates |

    - Functional Requirements

The control system shall provide:

- Automatic pump start and stop.

- Pump status indication.

- Water level monitoring and control.

- Borehole low-water protection.

- Reservoir/tank full protection.

- Generator and utility power interfacing (where applicable).

- Alarm monitoring and fault indication.

- Remote monitoring provision where specified.

- Event and operating data logging.

- Manual and automatic operating modes.

- Emergency stop function.

    - Protection Features

Minimum protection functions shall include:

- Incoming MCCB/ACB protection.

- Short-circuit protection.

- Overcurrent protection.

- Earth leakage protection.

- Overvoltage and undervoltage protection.

- Phase loss protection.

- Phase sequence protection.

- Surge protection devices (SPD).

- Overload protection.

- Control circuit protection.

- Lightning and grounding interface.

    - Compliance Requirements

| Low-Voltage Switchgear | IEC 61439 |
| --- | --- |
| Electrical Installations | IEC 60364 |
| Degrees of Protection | IEC 60529 |
| Electromagnetic Compatibility | IEC 61000 Series |
| Circuit Breakers | IEC 60947 |
| Surge Protection Devices | IEC 61643 |
| Control Equipment | IEC 60204 |
| Quality Management | ISO 9001 |
| Environmental Management | ISO 14001 |
| Occupational Health & Safety | ISO 45001 |

    - Documentation

The Contractor shall provide manufacturer data sheets, wiring diagrams, panel drawings, protection settings, factory test certificates, operation and maintenance manuals, as-built drawings, and warranty documentation for all supplied panels and control equipment.

  - AUTOMATIC TRANSFER SWITCHES

- Requirement

| ATS Type | Automatic Transfer Switch (ATS) |
| --- | --- |
| Applicable Standard | IEC 60947-6-1 |
| Number of Poles | 4-Pole (3P+N) |
| Voltage Rating | 400/230V AC |
| Frequency | 50 Hz |
| Current Rating | Minimum 125% of maximum load current |
| Rated Insulation Voltage | As per IEC standard |
| Short-Circuit Withstand Capacity | As per system fault level |
| Transfer Type | Automatic Utility/Generator Transfer |
| Source Selection | Utility – Generator |
| Neutral Pole | Fully Switched Neutral |
| Transfer Mechanism | Electrically Operated and Mechanically Interlocked |
| Manual Emergency Operation | Available |
| Automatic Generator Start Signal | Available |
| Automatic Generator Stop Signal | Available |
| Automatic Re-transfer to Utility | Available |
| Adjustable Time Delays | Available |
| Generator Warm-Up Delay | Adjustable |
| Generator Cool-Down Timer | Adjustable |
| Utility Return Delay | Adjustable |
| Voltage Sensing | Utility and Generator |
| Frequency Monitoring | Utility and Generator |
| Phase Failure Detection | Included |
| Phase Sequence Monitoring | Included |
| Under Voltage Protection | Included |
| Over Voltage Protection | Included |
| Under Frequency Protection | Included |
| Over Frequency Protection | Included |
| Source Availability Indication | Included |
| Source Connected Indication | Included |
| LCD Display | Digital LCD/HMI |
| Event Logging | Included |
| Alarm Indication | Included |
| Auto Mode Selector | Included |
| Manual Mode Selector | Included |
| Test Mode | Included |
| Communications Port | RS485/Modbus or Equivalent |
| Remote Monitoring Capability | Available |
| Control Voltage | As Recommended by Manufacturer |
| Enclosure Material | Powder-Coated Steel |
| Enclosure Rating Indoor | Minimum IP54 |
| Enclosure Rating Outdoor | Minimum IP65 |
| Cable Entry | Top/Bottom Gland Plate |
| Labels and Mimic Diagram | Included |
| Terminal Identification | Included |
| Factory Acceptance Test | Test Certificate Provided |
| Installation Accessories | Complete with Glands, Lugs and Terminations |
| Warranty | Minimum 24 Months |

- Functional Requirements

The ATS shall perform the following sequence automatically:

| Utility Failure | - Detect utility supply failure. - Initiate generators start signal. - Verify acceptable generator voltage and frequency. - Transfer load from utility to generator. - Continuously monitor generator operation. |
| --- | --- |
| Utility Restoration | - Detect restoration of utility supply. - Verify utility voltage and frequency stability. - Re-transfer load to utility supply after adjustable delay. - Operate generator cool-down timer. - Stop generator automatically. |
| Mandatory ATS Features | The ATS shall: - Be 4-pole type with switched neutral. - Be electrically operated and mechanically interlocked. - Prevent parallel connection of utility and generator sources. - Include adjustable transfer and re-transfer timers. - Include phase loss, phase sequence, voltage and frequency monitoring. - Include manual override/emergency operation. - Be suitable for continuous operation in ambient temperatures up to 50°C. - Be compatible with diesel generator automatic starting systems. - Include local indication lamps for: - Utility Available - Generator Available - Load on Utility - Load on Generator - ATS Fault |
| Bidder Submission Requirements | The bidder shall submit: - Manufacturer's ATS datasheet. - IEC 60947-6-1 compliance certificate. - General arrangement drawing. - Control schematic diagram. - Wiring diagram. - Short-circuit withstand rating certificate. - Factory routine test certificate. - Operation and maintenance manual. - Warranty certificate. |
| Acceptance Criteria | The ATS shall be considered technically compliant only if: - IEC 60947-6-1 certified. - 4-pole configuration with switched neutral. - Mechanical interlocking provided. - Automatic transfer and automatic re-transfer functions provided. - Generator auto-start interface provided. - Protection and monitoring functions fully compliant. - Minimum IP54 (indoor) or IP65 (outdoor) enclosure rating achieved. - Minimum 24-month warranty provided. |

  - MANUAL CHANGEOVER SWITCH (COS)

- General requirement

| Type | Manual Changeover Switch |
| --- | --- |
| Standard | IEC 60947-3 |
| Number of Poles | 4-Pole (3P+N) |
| System Voltage | 400/230V AC |
| Frequency | 50 Hz |
| Rated Current | Not less than 125% of maximum load current |
| Switching Positions | GRID – OFF – GENERATOR |
| Switching Type | Break-Before-Make |
| Mechanical Interlocking | Prevent simultaneous connection of grid and generator sources |
| Handle Type | Door-mounted, lockable rotary handle |
| Padlocking Facility | Provision for padlocking in all positions |
| Enclosure Material | Powder-coated galvanized steel |
| Enclosure Protection | IP54 minimum (Indoor) / IP65 (Outdoor) |
| Neutral Switching | Switched Neutral Included |
| Terminal Capacity | Suitable for specified cable sizes |
| Labelling | Permanent engraved labels for GRID, OFF and GENERATOR positions |
| Safety Shutters/Covers | Provided where applicable |
| Mounting Arrangement | Wall-mounted or panel-mounted |
| Operating Duty | Suitable for frequent manual operation |

- Mandatory ATS Features

The Manual Changeover Switch shall:

- Be a 4-pole, break-before-make type.

- Prevent back feeding between generator and utility sources.

- Have a mechanical interlock preventing simultaneous connection of two power sources.

- Include a clearly visible GRID-OFF-GENERATOR position indicator.

- Be lockable for maintenance and safety purposes.

- Be rated for the full load current of the pumping system with a minimum 25% spare capacity.

- Be installed in a weatherproof enclosure where located outdoors.

- Be suitable for operation in high-temperature and dusty environments typical of water supply installations.

- Bidder Documentation Requirements

The bidder shall submit:

- Manufacturer's datasheet.

- IEC 60947-3 compliance certificate.

- Rated current and short-circuit withstand data.

- Enclosure IP rating certificate.

- Dimensional drawings.

- Test certificates.

- Warranty certificate.

- Acceptance Criteria

The offered Manual Changeover Switch shall be considered technically compliant only if all mandatory requirements are met and supported by manufacturer documentation. Critical requirements include:

- IEC 60947-3 compliance.

- 4-pole configuration.

- Break-before-make operation.

- Mechanical interlocking.

- Adequate current rating.

- IP54/IP65 enclosure rating (as applicable).

- Minimum 24-month warranty.

# EARTHING AND LIGHTNING PROTECTION SYSTEM

    - EARTHING AND BONDING SYSTEM

- General

The Contractor shall design (where required), supply, deliver, install, test, commission, and hand over a complete Earthing and Bonding System for the facility.

The scope shall include, but not be limited to:

- Soil resistivity testing.

- Supply and installation of earth electrodes.

- Supply and installation of earth enhancement material.

- Supply and installation of underground earthing network (ring earth and earth mesh).

- Supply and installation of bare copper earthing conductors.

- Equi-potential bonding of all exposed metallic parts and electrical equipment.

- Bonding of transformers, inverters, panels, PV module support structures, cable trays, metallic enclosures, structural steel, fences, and gates.

- Earth inspection pits and test points.

- Exothermic welded connections.

- Earthing resistance testing and continuity testing.

- Preparation of as-built drawings and test reports.

- Training and handover.

The earthing system shall be designed to achieve an overall earth resistance of ≤ 5 Ohms or lower if required by local regulations.

Specifications

- Standards: IEC 60364; BS 7671; IEC/BS EN 62305-3

- Earth Electrodes

- Type: Copper-bonded steel earth rods.

- Diameter: Minimum 16 mm.

- Length: Minimum 1.5 m.

- Copper coating: Minimum 250 microns.

- Material Grade: RCS 1550 or approved equivalent.

- Installation method: Driven vertically into the ground.

- Connections: Exothermic welded only.

- Earth Grid Conductors

- Material: Bare stranded copper.

- Main earth grid conductor: Minimum 6 -120mm² as required by design

- Installation depth: Minimum 600 mm below finished ground level.

- Layout: Closed ring earth interconnected to form a mesh network.

- Bonding Conductors

- Material: Bare stranded copper or green/yellow insulated copper where exposed.

- Minimum size: 6 - 50 mm², as required by design

- Installed between earth grid and equipment.

- Earth Enhancement Material

- Type: Bentonite or approved low-resistance earth enhancement compound.

- Characteristics: Hygroscopic; Non-corrosive; Environmentally safe

- Applied around earth electrodes and in high soil resistivity areas.

- Equipment Bonding

The following equipment shall be bonded to the main earth grid:

- Transformers; Inverters; Main Distribution Boards (MDB); Sub Main Distribution Boards (SMDB); AC/DC Distribution Boards; PV module support structures; Cable trays; Structural steel; Generator sets; Metallic enclosures, and

- Perimeter fencing and gates

- Testing Requirements

  - Soil Resistivity Test: Wenner Four-Pin Method.

  - Earth Resistance Test: Fall-of-Potential Method. Final earth resistance ≤ 5 Ohms.

  - Continuity Test: Verification of all bonding conductors and earth connections.

    - Lightning protection system (LPS)

- General

The Contractor shall design (where required), supply, install, test, commission, and hand over a complete Lightning Protection System (LPS) for protection of personnel, buildings, equipment, and associated infrastructure from direct lightning strikes.

The scope shall include: Lightning risk assessment and protection design. Air termination network. Lightning rods (air terminals). Lightning conductors and catenary conductors (where applicable). Down conductors. Test clamps and disconnecting joints. Conductor supports and fixing accessories. Bonding of LPS to earthing system. AC Surge Protection Devices (SPD). Testing and commissioning. Documentation and training.

Technical requirements

- General

The Lightning Protection System shall be installed in accordance with IEC/BS EN 62305 requirements and shall be designed using the Rolling Sphere Method (RSM).

- Early Streamer Emission (ESE) air terminal or approved equivalent;

- Galvanized steel mast minimum 6 m high;

- Dedicated lightning earth system;

- Exothermically welded copper down conductors;

- Type I and Type II coordinated SPDs;

- Earth resistance ≤1 Ohm where achievable.

- Air Termination Conductors:

- Material: Hard drawn solid copper. Copper purity: 99.9% (C11000). Diameter: 10 mm minimum.

- Air Termination Rods (Air Masts)

- Material: Solid copper. Diameter: 10 mm minimum. Height: 500 mm minimum above support surface.

- Mounting: Stainless steel base and brackets.

- Supports and Fixings

- Material: SS304 stainless steel. Corrosion resistant.

- Suitable for outdoor installation.

- Down Conductors

- Material: Solid copper conductor. x-sectional area: Minimum 16-50 mm².

- Routing: Shortest practicable path. Straight vertical arrangement.

- Maximum spacing: Typically, 10 m around perimeter.

- Protection: PVC pipe up to 2.4 m above ground where exposed.

- Lightning Down-Conductor Sizes

| ≤15 kW | 25 mm², bare copper conductor |
| --- | --- |
| >15 – 45 kW | 35 mm², bare copper conductor |
| >45 – 132 kW | 50 mm², bare copper conductor |
| >132 – 250 kW | 70 mm², bare copper conductor |

- Test Clamps

- Type: Bi-metallic corrosion-resistant.

- Location: Approximately 1.0 m above finished ground level.

- Purpose: Isolation for testing and inspection.

- Lightning Protection Level

- To be determined through risk assessment and IEC 62305 calculations.

- Complete coverage shall be achieved using: - Air rods, Meshed conductors, Or catenary wire systems.

- AC Surge Protection Devices

- Main Distribution Board: Type 1 SPD (Class I). IEC 61643-11 certified. Coordinated with external lightning protection system.

- Sub Distribution Boards: Type 2 SPD (Class II). IEC 61643-11 certified.

- Testing Requirements

- Continuity Testing: Air termination network. Down conductors. Bonding connections.

- Visual Inspection: Supports. Fasteners. Exothermic joints. Test clamps.

- Functional Testing: Verification of complete connection to earthing system.

# SAFETY AND SECURITY WORKS FOR PV SYSTEM

  - LED SOLAR LIGHTING SYSTEM (ALL-IN-ONE TYPE)

- General

The Contractor shall supply, deliver, install, test, commission, and hand over complete solar-powered LED lighting systems for illumination of the solar power plant compound, access roads, and associated facilities.

The system shall be based on an All-in-One Solar Street Light Design integrating the following components into a single enclosure: LED luminaire; Solar photovoltaic panel; Rechargeable battery; MPPT charge controller; and Motion sensor and smart control electronics

The lighting system shall operate independently from the electrical grid, requiring no underground cabling between luminaires and power sources.

The Contractor shall provide all labor, materials, foundations, poles, fixtures, mounting hardware, testing equipment, documentation, and training required for a complete operational system.

- Applicable Standards

The equipment shall comply with the latest editions of applicable international standards or Equivalent internationally recognized standards shall be accepted, including:

| - IEC 60598 – Luminaires - IEC 62031 – LED Modules - IEC 61215 – Crystalline Silicon PV Modules - IEC 62109 – Safety of Power Converters | - IEC 60529 – IP Protection Ratings - IEC 62262 – IK Impact Ratings - ISO 9001 Certified Manufacturing |
| --- | --- |

- Technical Specifications

- Solar LED Luminaire

| LED Type | High-efficiency LED |
| --- | --- |
| Luminous Efficacy | ≥150 lm/W |
| Luminous Flux | 1,500–3,000 lumens minimum |
| Color Temperature | 4000K ± 500K |
| Color Rendering Index (CRI) | ≥70 |
| LED Lifetime | ≥50,000 operating hours |
| Housing Material | Die-cast aluminum alloy |
| Lens Material | UV-stabilized polycarbonate |
| Power Consumption | Optimized to meet autonomy requirements |
| Optical Distribution | Suitable for roadway/security lighting |

- Solar PV Module

| Technology | Monocrystalline Silicon |
| --- | --- |
| Module Efficiency | ≥20% |
| Nominal Power | 50–80 Wp minimum |
| Expected Service Life | ≥25 years |
| Encapsulation | Tempered glass and weather-resistant frame |
| Mounting | Integrated into all-in-one fixture |

The module shall fully recharge the battery under average site solar irradiation conditions.

- Battery Storage

| Battery Type | Lithium Iron Phosphate (LiFePO4) |
| --- | --- |
| Battery Management System | Integrated BMS |
| Autonomy | Minimum 2–3 nights without solar charging |
| Cycle Life | ≥2,000 cycles at 80% DoD |
| Depth of Discharge | Up to 80% |
| Expected Service Life | ≥5 years |
| Operating Temperature | -20°C to +60°C |

- Intelligent Controller

| Controller Type | MPPT |
| --- | --- |
| Charging Efficiency | ≥95% |
| Dusk-to-Dawn Operation | Automatic |
| PIR Motion Sensor | Integrated |
| Motion Detection Range | ≥8 m |
| Smart Dimming | Adjustable brightness profiles |
| Protection | Over-charge, over-discharge, short-circuit, reverse polarity |

- Pole and Mounting Structure

| Pole Height | 4–6 m |
| --- | --- |
| Material | Hot-dip galvanized steel |
| Galvanization Thickness | ≥80 microns |
| Wind Resistance | Minimum 150 km/h or project site requirement |
| Foundation | Reinforced concrete foundation |
| Mounting Bracket | Adjustable tilt and orientation |
| Fasteners | Stainless steel (SS304 or better) |

- Environmental Protection

| Ingress Protection | IP65 minimum |
| --- | --- |
| Impact Protection | IK08 minimum |
| Corrosion Resistance | Suitable for outdoor environments |
| Relative Humidity | Up to 95% non-condensing |
| Operating Temperature | -20°C to +60°C |

- Installation Requirements

The Contractor shall: Construct concrete foundations where required. Install poles, luminaires, and accessories. Ensure optimal orientation of solar panels. Verify mechanical stability and electrical integrity. Label each lighting unit with identification number. Carry out all civil and electrical works necessary for a complete installation.

- Testing and Commissioning

The following tests shall be conducted:

Factory Acceptance: Luminaire performance verification; Battery capacity verification; PV module inspection; Controller functional testing

Site Acceptance: Dusk-to-dawn functionality; PIR sensor operation; Battery charge/discharge verification; Structural stability assessment; Illumination coverage verification

- Warranty

The Contractor shall provide: Minimum 5-year warranty on complete lighting system.  Minimum 10-year performance warranty on solar panels. Availability of spare parts for at least 10 years.

    - PV CLEANING EQUIPMENT

- General

The Contractor shall supply, test, commission, and hand over a complete photovoltaic module cleaning system suitable for maintaining solar PV installations with a total capacity of up to 500 kWp.

The equipment shall remove dust, sand, bird droppings, and other contaminants without causing damage to PV modules.

The system shall support: Wet cleaning mode; Dry cleaning mode; Low-water-consumption operation; and Field deployment under harsh environmental conditions

- Applicable Standards

Equipment shall comply with: IEC 60335 – Equipment Safety; IEC 60529 – IP Ratings; CE Certification; ISO 9001 Quality Management; Applicable Occupational Health and Safety Standards

- Technical Specifications

| - Brush Module | Brush Material; Soft nylon/non-abrasive polymer. Brush Type; Cylindrical or multi-brush. Brush Width; Minimum 600 mm. Drive System; Electric motor. Speed Control; Variable. Housing; Lightweight corrosion-resistant material. Replaceable Brushes; Yes. |
| --- | --- |
| - Treatment system | Water Source; Integrated storage tank. Water Purification; RO or Ion Exchange. Water Conductivity; <10 μS/cm. Water Filter; Integrated pre-filter. Pump Type; Low-flow, efficient pump. Spraying Method; Atomized low-pressure spray. Water Consumption; ≤0.5 liters per panel. |
| - Power System | Power Supply; Rechargeable battery. Battery Type; Lithium-ion or equivalent. Operating Time; ≥8 hours continuous operation. Charging Method; AC charger and/or solar charging. Charging Time; ≤8 hours. |
| - Control System | Control Interface; User-friendly control panel. Cleaning Modes; Wet and Dry. Speed Adjustment; Yes. Water Flow Adjustment; Yes. Emergency Stop; Required. Low Water Alarm; Required. Overload Protection; Required. |
| - Mechanical | Handle Type; Telescopic. Reach; 4–6 m minimum. Weight; Maximum 8 kg for handheld cleaning head. Frame Material; Aluminum alloy or equivalent. Corrosion Resistance; Outdoor rated. |
| - Environmental | Operating Temperature; -5°C to +50°C. Dust Resistance; High-dust environments. Relative Humidity; Up to 95%. IP Protection; IP54 minimum. |
| - Accessories | The supply shall include: One-year supply of replacement brushes. One-year supply of replacement filters. Maintenance tool kit. Storage case and/or trolley. Water hoses and fittings. Battery charger. Spare seals and consumables. |
| - Warranty and Support: | Minimum 2 years |

- Testing and Training:

The Contractor shall provide:

- Factory Documentation: Factory acceptance test reports. Equipment inspection certificates. Quality assurance documentation.

- Site Verification: Demonstration of cleaning capability. Water consumption verification. Functional testing of controls and safety features.

- Training: Minimum one-day onsite training covering: Equipment operation; Routine maintenance; Safety procedures; Troubleshooting

    - FIRE EXTINGUISHERS

- General

Supply, deliver, install, test, commission, and hand over portable ABC Dry Chemical Powder (DCP) fire extinguishers complete with wall mounting brackets, identification signage, inspection tags, and all accessories required for a complete and operational fire protection system.

- Type: Portable ABC Dry Chemical Powder Fire Extinguisher

- Extinguishing Agent: Mono Ammonium Phosphate Dry Powder

- Suitable for: Class A, B, and C Fires

- Cylinder Material: Seamless steel cylinder with corrosion-resistant finish

- Operating Pressure: As per manufacturer's standard

- Pressure Gauge: Included

- Discharge Hose and Nozzle: Included

- Mounting: Wall-mounted with steel bracket

- Certification: Comply with EN 3, BS EN 3, UL, or equivalent approved standards

- Identification Label: Factory-applied operating instructions and fire classification markings

- Warranty: Minimum 1 year

- Installation

  - Secure mounting of extinguishers on walls or dedicated floor stands near the solar inverter units (maximum travel distance of 15 meters).

  - The handle should be mounted 1 – 2m from the floor for easy access.

  - A clear path of at least 1 meter must be maintained around the extinguishers. Units must be inspected monthly for pressure loss (Powder) or weight loss

- Signage:

Supply and fixing of photoluminescent (glow-in-the-dark) ID signs above each unit indicating the type of fire they are suited for (e.g., "Safe for Live Electrical Equipment").

- Certification: Provision of valid inspection tags and pressure test certificates.

- Warranty: at least two years.

# BOREHOLE CASINGS, PIPES, AND WELLHEAD ACCESSORIES

    - GENERAL

This Service Package covers the engineering (where applicable), procurement, manufacture, supply, transportation, installation(where applicable), testing, commissioning, and warranty support for borehole casing systems, well screens, rising mains, transmission pipelines, distribution pipelines, valves, fittings, mechanical accessories, and associated appurtenances required for groundwater abstraction and water conveyance systems under UNICEF-supported water supply projects throughout Ethiopia.

The Contractor shall supply borehole casing pipes, well screens, centralizers, gravel pack accessories, wellhead assemblies, rising mains, HDPE, ductile iron, galvanized steel, stainless steel, or uPVC pipelines, together with all valves, fittings, couplings, reducers, expansion joints, flange adaptors, dismantling joints, air valves, pressure reducing valves, non-return valves, scour valves, and other accessories required for a complete and functional system. All products shall be manufactured in accordance with recognized international standards and certified for potable water applications.

Where installation is included, the Contractor shall carry out all mechanical works required for pipeline construction, borehole completion, wellhead installation, valve chamber installation, pipeline jointing, anchorage, thrust restraint, pressure testing, flushing, disinfection, and commissioning. Installation shall be carried out using approved procedures and qualified personnel to ensure the integrity and long-term performance of the system.

Upon completion of installation, the Contractor shall conduct hydraulic pressure tests, leakage tests, flushing, disinfection, and operational verification to demonstrate compliance with the design pressure, flow capacity, and operational requirements. The Contractor shall prepare all inspection records, test reports, as-built drawings, operation manuals, warranty certificates, and maintenance recommendations necessary for successful project handover.

The Contractor shall provide warranty services and technical support during the warranty period and shall replace any defective materials or workmanship at no additional cost to the Employer.

    - BOREHOLE RISER PIPE & ACCESSORIES

- General

The work under this section includes the supply, delivery, handling, installation, and testing of borehole riser pipes for use with submersible pump installations. The scope shall cover, but not be limited to, the following:

- Supply of riser pipes made of uPVC (PN16) or stainless steel (AISI 304/316) depending on borehole water chemistry, complete with necessary joints, couplings, and accessories.

- Delivery and safe handling of all riser pipes to the site, ensuring protection against damage, contamination, and deformation.

- Installation of riser pipes within the borehole, including:

  - Proper alignment with the submersible pump outlet.

  - Secure and watertight jointing using threaded couplings, flanges, or rubber sealing rings.

  - Provision of column clamps and pump support brackets at the wellhead.

  - Ensuring riser pipes are installed vertically, without strain or misalignment.

- Accessories: Installation centralizers, pump adapters, clamps, and other fittings required for proper functioning.

- Testing and Commissioning: Pressure testing of riser pipe assembly to confirm leakage-free installation. Verification of mechanical strength to withstand dynamic load and vibration during pump operation.

- Documentation and Handover: Submission of manufacturer’s certificates, test results, and as-built installation. Marking of installed riser pipe materials for traceability.

- The Contractor shall supply, deliver, install, and test all required borehole accessories and fittings as part of the pumping system. The works shall include but not be limited to:

  - Pressure Gauges: Supply and installation of calibrated, corrosion-resistant pressure gauges at the discharge manifold, suitable for continuous monitoring of system pressure.

  - Non-Return Valves (NRV): Supply and installation of heavy-duty non-return valves to prevent backflow and protect pumps.

  - Water Meters (WM): Supply and installation of mechanical or electromagnetic type water meters for accurate measurement of borehole discharge.

  - Bends and Elbows: Supply of galvanized steel or ductile iron bends/elbows (45° and 90°) for connecting rising mains and delivery pipes.

  - Couplings/Joints/Unions: Supply of threaded/flanged couplings and flexible joints for secure, watertight, and vibration-resistant connections.

  - Ancillary Fittings: Provision of gaskets, bolts, nuts, washers, sealing compounds, and other accessories required for proper installation.

- Installation and Testing:

  - Proper alignment and watertight installation of all fittings.

  - Testing for leakage and pressure tightness at rated working pressure.

  - Calibration of instruments (pressure gauges and water meters).

- Material specification

- GI Carbon Steel Raiser Pipes

- Materials: Hot dip galvanized Carbon Steel according to BS 1387 or equivalent

- Joint Type: Threaded or Flanged

- Thickness / Schedule: Heavy as per BS 1387 standard or equivalent.

- Single Piece Length: 6 m, 3m length is acceptable.

- Pipes package shall include all required adaptors and accessories

- Stainless Steel Riser Pipe and ZSM coupling:

- Grade SS 1.4301 (AISI 304), Seamless/Welded

- Includes integrated ZSM connection system for rapid assembly.

- EPDM O-ring seals, stainless steel shear springs, and locking mechanisms

- Complete with Pump-to-Riser Adaptor Pipe with ZSM coupling interface

- Diameter: DN50 - DN100, Length: 6m Pressure rating: PN10 – PN16

- Stainless Steel Pipe and threaded/flanged joint:

- Heavy-duty Grade SS 1.4301 (AISI 304), Seamless/Welded, L = 6000 mm

- Complete with Full set of heavy-duty flanged/Treaded couplings

- Complete with Pump-to-Riser Adaptor Pipe with flanged/Treaded coupling interface

- Diameter: DN50 - DN100, Length: 6m Pressure rating: PN10 – PN30

- Riser pipe Downhole Support accessories:

Each supplier of the riser pipes shall include the following

- Heavy-duty Polypropylene (PP) cable clamps and Riser guide brackets

- Size suitable for DN50 up to DN150 pipe

- Secure power and control cables to the riser, at every 3m

- Quantity Required: 1 per 3m or 2 pcs per 6m supplied riser pipe

    - WELLHEAD OUTLET MANIFOLD & APPURTENANCES

- General

The Contractor shall design (where applicable), supply, transport, install, test, commission, and hand over a complete borehole wellhead outlet manifold assembly including all valves, fittings, instrumentation, supports, accessories, anchorages, and ancillary pipework necessary for safe and reliable operation of the borehole pumping system. The complete manifold shall be delivered as a fully operational system.

The wellhead outlet manifold shall provide:

- Pump isolation.

- Flow measurement.

- Pressure monitoring.

- Air release.

- Surge protection.

- Sampling facilities.

- Pressure regulation and relief.

- Connection to the transmission/distribution pipeline.

- Materials specification

- Manifold Pipework: The manifold pipework shall be manufactured from:

- Hot Dip Galvanized Carbon Steel (HDG)

- Stainless Steel AISI 304

- Stainless Steel AISI 316 (where aggressive water conditions exist)

- Requirements: All fabrication welding shall be completed before galvanizing.

| Standard | ISO 65, EN 10255, BS 1387 or equivalent |
| --- | --- |
| Pressure Class | PN16 minimum (PN25/PN30 where required) |
| Nominal Diameter | DN50 – DN150 |
| Pipe Ends | Flanged |
| Coating | Hot Dip Galvanized ≥85 µm |
| Fabrication | Shop Welded |

- Manifold Flanges

| Standard | EN 1092-1 |
| --- | --- |
| Rating | PN16, PN25 or PN30 |
| Material | Carbon Steel HDG or Stainless Steel |
| Facing | Raised Face (RF) |
| Bolting | High Tensile Steel Grade 8.8 or Stainless Steel A2/A4 |

- Gaskets

| Material | EPDM Rubber |
| --- | --- |
| Thickness | 3 mm minimum |
| Water Approval | Suitable for potable water |
| Pressure Class | Matching flange rating |

- Mandatory Manifold Components

The wellhead manifold shall comprise the following minimum components.

| - Riser Head Connection | A connection assembly shall be installed between the borehole riser pipe and the manifold. - Material: HDG Steel or Stainless Steel - Flanged adaptor. - Pipe collar. - Support flange. - Wellhead sealing arrangement. |
| --- | --- |
| - Vertical riser pipe Extension | A vertical extension spool shall connect the borehole riser to the manifold. Material; HDG Steel or Stainless Steel. Length; As per approved drawings. Rating; PN16 minimum. |
| - Dismantling Joint | A dismantling joint shall be provided for removal and replacement of: Valves. Flow meter. Check valve. Type; Adjustable Flanged. Body; Carbon Steel/DI. Rods; Galvanized or Stainless Steel. Pressure Rating; PN16 minimum. |
| - Main Isolation Gate Valve | Type; Resilient Seated Gate Valve. Standard; BS 5163. Body; Ductile Iron GJS500. Coating; Fusion Bonded Epoxy. Operation; Hand Wheel. Pressure Class; PN16 minimum. |
| - Non-Return Valve | Type; Swing Check Valve. Standard; BS 5153. Body; Ductile Iron. Disc; Stainless Steel / EPDM. Pressure Rating; PN16 minimum. |
| - EM Flow Meter | Type; Full-Bore Electromagnetic. Protection; IP68. Accuracy; ±0.5% or better. Lining; Hard Rubber / EPDM. Electrodes; SS316. Output; Digital. Power Supply; Solar Compatible. Accessories:; Grounding rings. Converter. Display. Flanges. Mounting hardware.. Straight pipe Length; Upstream: minimum 5D Downstream: minimum 3D.. |
| - Air Valve Assembly | - Components: Air release valve; Isolation valve; Branch spool; and Drain connection. - Technical requirements: Type; Double Orifice. Size; DN50. Pressure Rating; PN16. Body; Ductile Iron. Internal Parts; Stainless Steel. |
| - Pressure Instrumentation Assembly |  |
| - Pressure Gauge | Type; Analog. Housing; Stainless Steel. Dial; 100 mm. Accuracy; Class 1.6. Range; According to system pressure. |
| - Pressure Switch | Contacts; NO/NC. Protection; IP65. Connection; 1/2" NPT. Function; High/Low Pressure. |
| - Sampling Assembly | - A water sampling point shall be installed. - Components: - 1" stainless steel branch. - Pressure reducing valve. - Isolation valve. - Sampling tap, and - Unions. - Material: Stainless Steel 304 minimum. |
| - Pressure Relief Valve | Type; Pilot Operated. Pressure Rating; PN16 minimum. Body; Ductile Iron. Trim; Stainless Steel. Function; Surge and Overpressure Protection. Complete with; isolation valve and discharge pipework.. |
| - Surge Vessel System | Type; Bladder Type. Capacity; 2 m³ minimum. Bladder Material; Food Grade Butyl. Connection; DN80 PN16. Vessel Material; Carbon Steel Epoxy Coated. Complete with:; - Isolation valve. - Dismantling joint. - Pressure gauge. - Charging valve. - Supports.. |
| - Pipe Supports | All manifold pipework shall be supported using: - Hot-dip galvanized steel supports. - Anchor blocks where required. - Adjustable clamps. Stainless steel fasteners Supports shall prevent: Vibration. Sagging. Excessive stress. |

- Installation Requirements

The Contractor shall: Align all pipework accurately. Prevent flange stresses. Install all valves in accessible positions. Support all equipment independently. Ensure flow direction markings are correct. Install instruments in visible locations. Protect all exposed threads and connections.

- Testing and Commissioning

- Hydrostatic Testing: Test pressure shall be: 1.5× Max. Working Pressure; Duration: 2hr Min.

- Acceptance Criteria: No leakage. No pressure loss. No visible deformation.

- Functional Testing: The Contractor shall demonstrate: Valve operation. Flow meter operation. Pressure gauge accuracy. Air valve performance. Pressure switch operation. PRV setting verification. Surge vessel operation.

- Documentation and warranty

The Contractor shall submit: Manufacturer's catalogues. Material certificates. Calibration certificates. Pressure test certificates. Coating certificates. Shop drawings. As-built drawings. O&M manuals. Spare parts recommendations. Warranty documents (Minimum 24 Months from commissioning.)

Notes

Standard Manifold Composition (Example: DN100 PN16 Assembly) includes:

- Riser head connection; 4.5 m DN100 manifold pipework; 2 No. 90° bends; 1 No. 45° bend; 2 No. dismantling joints; 1 No. DN100 gate valve; 1 No. DN100 NRV; 1 No. DN100 electromagnetic flow meter; Air valve assembly; Sampling assembly; Pressure gauge; Pressure switch; Surge vessel; Supports and anchors; Flanges and gaskets

- The Contractor's lump-sum rate covers all these items.

The material designation (HDG Carbon Steel or Stainless Steel 316) shall apply to all manifold pipework, fabricated spools, bends, reducers, branches, supports, and fittings. Valves, flow meters, instrumentation, surge vessels, gaskets, bolts, nuts, and other appurtenances shall be supplied in accordance with the technical specifications regardless of manifold material type.

    - WELLHEAD COVER ASSEMBLY

- General

The Contractor shall design (where applicable), supply, fabricate, deliver, install, test, commission and hand over a complete Wellhead Cover Assembly for boreholes, including all structural, mechanical and sealing components required to provide a secure, watertight, corrosion-resistant and maintainable borehole headworks system.

The Wellhead Cover Assembly shall protect the borehole against: Surface water ingress. Contamination. Unauthorized access. Entry of insects, rodents, and foreign materials. Mechanical damage to riser pipes, cables and instrumentation.

The Works shall include, but not be limited to: Wellhead cover plate. Wellhead ring frame. Pipe collar and riser interface. Cable and sensor penetrations. Vent assembly. Rubber seals and gaskets. Locking arrangement. Lifting provisions. Anchor bolts and fastening system. Corrosion protection. Installation, testing and commissioning.

The Contractor shall provide all materials, labor, tools, equipment, transportation, consumables and accessories necessary for a complete operational installation.

- Construction material selection

The Wellhead Cover Assembly shall be manufactured from one of the following materials:

| Option A – HDG Carbon Steel | Base Material: Mild Steel ASTM A36 or equivalent. Corrosion Protection: Hot-Dip Galvanized. Standard: ISO 1461 or equivalent. Zinc Coating Thickness: Minimum 85 μm. |
| --- | --- |
| Option B – Stainless Steel | Material Grade; AISI 316 / EN 1.4401. Finish; Pickled and Passivated. Fasteners; Stainless Steel A4-70 minimum. |

NOTE: Where groundwater or environmental conditions are corrosive, Stainless Steel 316 shall be used.

- Technical Specifications

| - Wellhead Cover Plate: | The cover plate shall form the primary protective barrier over the borehole. Material; HDG Steel or SS316. Thickness; 18 mm Minimum. Shape; Circular. Diameter; Not less than borehole casing OD + 100 mm. Finish; Smooth, burr-free edges. Surface; Non-slip finish preferred. Features; The cover plate shall be provided with: • Foldable lifting handles. • Locking arrangement. • Pipe penetration opening. • Cable entry points. • Sensor entry openings. • Ventilator opening. • Identification plate.. |
| --- | --- |
| - Wellhead Ring Frame | The ring frame shall provide structural support and a sealing interface between the borehole casing and the cover plate. Requirement. Material; HDG Steel or SS316. Construction; Fabricated circular frame. Alignment; Centrally aligned with casing. Fixing; Bolt-down or welded connection. Corrosion Protection; As specified. Features; The ring frame shall be supplied c/w: • Anchor fixing points. • Gasket support surface. • Bolting arrangement. • Alignment brackets.. |
| - Pipe Collar Assembly | A pipe collar shall be provided for the riser pipe passage through the cover. Material; HDG Steel or SS304 or SS316. Connection; Threaded, Flanged or ZSM-compatible. Diameter; Match riser pipe; DN50–DN150. Pressure Rating; Match riser pipe rating, 16bar Min. Seal; EPDM Rubber Gasket. The collar assembly shall prevent ingress from contaminants while allowing safe pump removal.. |
| - Vent Assembly | The cover shall include a permanent vent assembly. Pipe Diameter; Minimum 25 mm. Material; Stainless Steel. Insect Screen; SS316 Mesh. Weather Protection; Rain Hood. Position; Above cover level. The vent shall permit air movement while preventing entry of insects and debris.. |
| - Cable and Entry Ports | The cover shall include sealed entries for: Power cables. Control cables. Water level probes. Pressure sensors. SCADA instrumentation. Entry Type; Cable gland. Material; Brass Nickel-Plated or Stainless Steel. Protection; IP68 Minimum. Seal Material; EPDM/NBR. Unused ports shall be sealed using blanking plugs.. |
| - Gasket and Sealings | A continuous sealing system shall be provided between the cover plate and ring frame. Material; EPDM Rubber. Thickness; Minimum 5 mm. Water Quality; Suitable for potable water. Service Life; Minimum 10 years. The gasket shall provide a watertight and dust-proof seal.. |
| - Locking System | The cover assembly shall be equipped with security locking arrangements Requirements: Stainless steel locking hasp. Looking eye for padlock. Tamper-resistant hardware. Corrosion-resistant components. |
| - Lifting Arrangement | The cover shall include integrated lifting provisions. Requirements: Minimum two lifting handles. Fold-down type preferred. Capable of supporting full cover weight. Suitable for removal using manual lifting equipment. |
| - Identification Plate | A permanent identification plate shall be fixed to the cover. Information to be Displayed: Borehole reference number. Borehole depth (m). Casing diameter. Pump capacity (m³/hr). Installation date. Owner/Operator. Material: Stainless steel engraved plate. |
| - Fabrication Requirements | The Contractor shall submit shop drawings for approval prior to fabrication. Full compatibility with borehole casing. Smooth finishing. Correct alignment of openings. Proper sealing surfaces. High-quality welding. All welds shall be continuous and free from defects. |
| - Installation Requirements | The Contractor shall: Align the ring frame centrally over the casing. Securely fix the frame to the well chamber or concrete plinth. Install gaskets and seals. Fit the cover plate without distortion. Test locking arrangements. Ensure watertight installation. Seal all cable and instrument entries. |
| - Testing and Commissioning | Visual Inspection to verify: Material compliance. Surface finish. Correct dimensions. Coating quality. Alignment. Functional Testing to verify: Opening and closing of cover. Locking system operation. Cable gland sealing. Vent functionality. Water Tightness Test shall demonstrate: No water ingress. No visible leakage. No opening deformation. |
| - Documentation | The Contractor shall submit: Material certificates. Galvanizing certificates (for HDG units). Stainless steel grade certificates. Fabrication drawings. Installation records. Inspection reports. As-built drawings. Warranty certificates. |

- Measurement and Payment

Unit of Measurement: Set

Basis of Payment: The rate shall include all materials, fabrication, protective coatings, fasteners, seals, vents, cable glands, lifting devices, locking systems, installation, testing, documentation and all incidental works required for a complete Wellhead Cover Assembly. No separate payment shall be made for bolts, nuts, washers, welding, stiffeners, gaskets or ancillary fittings.

    - BOREHOLE CASING & ACCESSORIES

- General requirement

Borehole casing pipes shall be manufactured from high-quality steel or uPVC (depending on hydrogeological conditions and project requirements).

All pipes shall be new, straight, smooth, and free from cracks, dents, blisters, or other defects.

Pipes must conform to ISO, ASTM, or equivalent international standards.

Joints must ensure a watertight and corrosion-resistant connection.

- Pipes shall be designed to withstand external earth pressures, water table variations, and installation stresses.

- Performance

- Minimum pressure rating: PN10 (10 bar) for uPVC; ≥ 10 bar working pressure for steel.

- Collapse resistance is sufficient to withstand external hydrostatic pressure at maximum borehole depth.

- Resistance to impact, abrasion, and chemical attack.

- Quality Assurance: Pipes must be factory tested for:

- Dimensional accuracy

- Hydrostatic pressure resistance

- Collapse resistance

- Thread/joint leakage tests

- Manufacturer’s test certificates need to be provided.

- Pipes must bear manufacturer’s mark, diameter, wall thickness, pressure class, and standard reference.

- Borehole Casing Material Specifications

- uPVC Casing Pipes

- Manufactured from unplasticized polyvinyl chloride (uPVC) suitable for potable water applications.

- Comply with ASTM D1785, DIN 4925, ISO 4422 or equivalent.

- Free from harmful substances, resistance to corrosion, chemicals, and electrolytic action.

- Designed for a minimum service life of 50 years under normal operating conditions.

- Conforming to pressure rating ≥ PN10 (10 bar).

- Wall thickness: ≥6 mm (≤150 mm dia.), 8–12 mm (200–300 mm dia.)

- Steel Casing Pipes

- Material: High-strength carbon steel, seamless or ERW (Electric Resistance Welded).

- Standard: API 5L / ASTM A53 / DIN 2440 or equivalent.

- Internal and external surfaces coated with anti-corrosion epoxy or galvanization.

- Minimum yield strength: ≥ 240 MPa.

- Wall thickness: ≥6 mm (≤250 mm dia.), 8–12 mm (>250 mm dia.)

- Dimensions and Tolerances

- Nominal Diameter:  As per borehole design (commonly 150 mm – 400 mm internal diameter).

- Straightness Tolerance: Deviation not to exceed 1 mm per meter length.

- Straightness tolerance: ≤1 mm per meter length

- Length of Each Pipe: 3 m or 6 m standard (with threaded/coupled or flush joints).

- Screen Sections

- Borehole screens shall be made from the same material as casing pipes.

- Slot sizes: Typically, 0.5 mm – 1.0 mm, selected based on aquifer grain-size analysis.

- Open area: Minimum 10% of screen surface area.

- Screen length as per borehole design, placed at aquifer zone.

- Joints and Connections

  - uPVC Pipes:

- Should have male-female threaded ends with square-cut threads.

- Threads are protected with rubber or PTFE sealing rings.

- Factory-supplied couplers with the same strength as the pipe.

  - Steel Pipes:

- Butt-welded or threaded & coupled joints with API standard threads

- Thread connections must be supplied with thread protectors.

    - PIPES AND FITTINGS

- General

This specification covers the supply, delivery, installation, jointing, testing, disinfection, commissioning, and warranty for the potable water transmission mains and distribution network Pipes, fittings, valves, and accessories. The scope includes all excavation, backfilling, and compaction works.

- System Pressure Rating: All components shall be rated for a minimum working pressure of PN16 (16 bar). Higher ratings (PN20, PN25) may be required for specific transmission sections.

- Hydraulic Capacity: Pipes shall be sized to maintain flow velocities between 0.5 m/s and 2.5 m/s.

- Water Quality: All materials shall be certified for potable water contact (e.g., WRAS, NSF/ANSI 61).

- Submittals: The Contractor shall submit the following for approval:

- Manufacturer's technical data sheets and material certificates.

- Pipe samples and jointing statements.

- Type test certificates for pipes, fittings, and valves.

- Detailed trench design and pipe laying procedure.

- Pressure testing and disinfection procedure.

- Installation, operation, and maintenance (IOM) manuals.

- Material specifications - Pipe & fitting

Pipe Materials:

| DCI Pipe | (Ductile cast Iron Pipe): - Standard: EN 545 or AWWA C151. - Lining: Cement mortar lining internally, polyethylene sleeving or bituminous coating externally. - Joints: Push-fit TYTON® type or flanged. - Sizes: DN 80 to DN 1200 |
| --- | --- |
| HDPE Pipe | (High density Polyethylene Pipe): - Standard: ISO 4427, PE 100. - Joints: Butt fusion (preferred) or electrofusion. - Sizes: OD 20mm to OD 1200mm (PN16 rated) |
| u-PVC Pipe | (Polyvinyl Chloride (PVC) Pressure Pipe): - Standard: AWWA C900, Class 150 or 200. - Joints: Solvent cement or rubber ring gaskets. - Sizes: 4" to 12" (100mm to 300mm) |
| GRP Pipe | (Glass Reinforced Plastic Pipe): - Standard: ISO 14692 or AWWA C950. - Joints: O-ring bell and spigot or flanged. - Sizes: DN 500 to DN 2000+ (for large transmission mains) |

- Fitting & valves: Shall be of the same material and pressure rating as the connecting pipe

| Pipe Fittings: | Elbows (90°, 45°, 22.5°); Tees (equal, reducing), reducers, caps, flanged adapters. Ductile Iron: Shall be cement-lined and EN 545 or AWWA C110/A21.10 HDPE: Butt fusion or electrofusion types from the same manufacturer as the pipe |
| --- | --- |
| Gate Valves | Type: Resilient wedge, non-rising stem, flanged ends. Standard: AWWA C509 or EN 1074. Material: Ductile iron body, bronze/SS trim, EPDM seat. Operation: Handwheel (for smaller sizes) or geared actuator (for sizes > DN300). |
| Butterfly Valves | Type: Double flanged, lugged or wafer type, resilient seated. Standard: AWWA C504 or EN 593. Material: Ductile iron body, 316 SS disc & shaft, EPDM seat. Operation: Lever, gearbox, or electric actuator. |
| Check Valves | Type: Swing check or wafer type check valve. Standard: AWWA C508 or API 6D. Material: Ductile iron body, 316 SS disc & hinge pin. |
| Air Valves: | Type: Combination air valve (large orifice for air release, small orifice for air vacuum). Standard: BS EN 1074-4. Sizing & Location: To be provided at all high points in the pipeline. |
| Drain Valves: | Type: Resilient seated gate valve or ball valve. Location: To be provided at all low points in the pipeline. |
| Hydrants: | Type: Dry barrel fire hydrant with two hose connections and one pumper connection. Standard: AWWA C502 or BS 750. Valve: Gate valve operation. |

- Installation, Testing & commissioning

| Installation: | Trench: Excavate trench to required line and level. Bedding: Provide minimum 100mm of selected granular bedding material. Jointing: Lay pipes on the prepared bedding. Execute jointing per manufacturer's instructions under qualified supervision. Backfilling: Backfill in layers with selected material. Compact to 95% Modified Proctor Density. Reinstate surfaces to original condition. |
| --- | --- |
| Pressure Test: | Test each pipeline section at 1.5 times the design working pressure for a duration of 2 hours. The test is successful if the pressure drop is within allowable limits. |
| Disinfection: | Disinfect the entire pipeline using a chlorination method (e.g., tablet or slug dose) to achieve a concentration of 50 ppm for 24 hours. Flush thoroughly until chlorine residual and turbidity meet potable water standards. |
| Commissioning: | Upon successful testing and disinfection, commission the system into operation. Hand over all record drawings ("as-built" drawings), test reports, valve operation keys, and operation/maintenance manuals |
| Warranty: | The supplier shall provide a comprehensive warranty for a period of: - Pipes & Fittings: 10 years against defects in materials and workmanship. - Valves & Appurtenances: 2 years from the date of successful commissioning. |

# CIVIL AND STRUCTURAL RELATED WORKS

  - GENERAL SCOPE OF WORK

The Contractor shall provide all labor, materials, tools, equipment, supervision, transportation, testing, quality control, and incidentals necessary for the complete construction and installation of the civil and structural works associated with the Solar PV Water Pumping System.

The works shall include, but not be limited to:

- Design verification, supply, fabrication, delivery, and installation of hot-dip galvanized steel PV mounting structures.

- Supply and install security fencing and access gates around the PV compound.

- Construction of reinforced concrete foundations for PV mounting structures.

- Construction of concrete foundations/pedestals for pumps, control panels, diesel generators, and associated equipment.

- Construction of valve chambers, manholes, and inspection chambers complete with covers.

- Testing, inspection, quality assurance, and preparation of as-built drawings.

- Standards

All civil and structural works shall comply with the latest editions of applicable standards, including:

- EN 1990 – Eurocode Basis of Structural Design

- EN 1991 – Actions on Structures

- EN 1992 – Design of Concrete Structures

- EN 1993 – Design of Steel Structures

- ISO 1461 – Hot Dip Galvanizing

- ISO 898-1 – Mechanical Properties of Fasteners

- ASTM Standards for materials and testing

- ACI 318 – Structural Concrete

- Ethiopian Building Code Standards (where applicable)

- Design Submissions

Before commencement of works, the Contractor shall submit for approval: Structural calculations. Foundation design calculations. Shop drawings. Fabrication drawings. Reinforcement details. Foundation layouts. Material certificates. Galvanization certificates

No fabrication shall commence before approval by the Engineer.

- Excluded Works:

The following activities are explicitly excluded from the Contractor's scope:

- Bulk site clearing.

- Site grading and leveling.

- Earth filling and cut-to-fill operations.

- Removal of large vegetation and trees outside the work footprint.

- Major rock excavation is not directly associated with foundation construction.

The Client shall hand over the site in a condition suitable for installation of the PV system and associated facilities.

The Contractor shall only be responsible for removal of debris generated by its own construction activities and minor clearing required immediately within the foundation footprint.

  - MODULE MOUNTING STRUCTURE

    - Scope of the Work

- Supply, design verification, manufacture, transport, install, test and commission complete Ground-Mounted Fixed Tilt Module Mounting Structures (MMS) for installation of 650Wp photovoltaic modules as indicated in the Tender Drawings and approved shop drawings.

- The mounting structures shall be based on a single central column support arrangement and shall accommodate:

  - Type-1 MMS: 2 Portrait × 8 Modules (16 Modules/Table)

  - Type-2 MMS: 2 Portrait × 2 Modules (4 Modules/Table)

- The attached Tender Drawing shall be considered as the reference prototype for the mounting system. The Contractor shall verify the structural design and dimensions and submit complete structural calculations, foundation calculations, wind load calculations, assembly drawings, shop drawings and foundation layout drawings for approval prior to fabrication.

- The structure shall consist of a single central column, rafters, purlins, bracing members, column extensions, cleats and connection members, all fabricated from cold-formed galvanized steel C-channel sections.

- The mounting structure shall be designed for a minimum wind speed of 50 m/s (180 km/hr) and shall withstand all applicable dead loads, live loads, wind loads and seismic effects in accordance with applicable standards.

- The structure shall be fixed-tilt ground mounted with a tilt angle between 10° and 15° as detailed in the Tender Drawings.

- The minimum front clearance from the lowest module edge shall be 1.0 m, and the maximum rear structure height shall not exceed 2.2 m.

- The work shall include supply and installation of all structural members, connectors, anti-theft module fixing hardware, stainless steel fasteners, anchor systems, templates, reinforced concrete foundations and all accessories necessary for a complete installation.

- All components shall be factory prefabricated using CNC cutting and punching processes. Site cutting, drilling, punching, welding or modification of galvanized members shall not be permitted.

- The Contractor shall provide Mill Test Certificates, Galvanizing Certificates, Factory Acceptance Test Reports, Installation Manuals, O&M Manuals, Warranty Certificates and As-Built Drawings.

    - Dimensions and Access Requirements

- The MMS dimensions shall generally comply with the attached Tender Drawings and approved shop drawings.

- The horizontal distance between adjacent MMS tables shall not be less than 1.0 m unless otherwise approved by the Engineer.

- The spacing between adjacent PV modules shall not be less than 25 mm.

- The minimum front ground clearance shall be 1000 mm from the lowest module edge.

- The structure shall provide adequate access for module inspection, maintenance and cleaning.

- The mounting system shall be oriented south facing with a fixed tilt angle of 10° to 15°, unless otherwise indicated in the approved layout.

    - Material Specification

Structural Steel Members

All structural steel members shall be manufactured from S355 Structural Grade Steel and shall consist of cold-formed lipped C-channel sections as detailed in the Tender Drawings and approved shop drawings.

| Member | Section |
| --- | --- |
| Main Central Column | C100×50×3 mm |
| Rafters | C80×50×2 mm |
| Purlins | C80×40×2 mm |
| Front Bracing | C80×40×2 mm |
| Back Bracing | C80×40×2 mm |
| Column Extension | C80×40×2 mm |
| Purlin Splice/Connector | C70×40×4 mm |
| Bracing Connector | C80×40×2 mm |
| Cleats | L70×40×4 mm |

- The MMS shall utilize a single central column arrangement supporting the complete PV table assembly.

- All C-channel sections shall be free from distortion, cracks, laminations and manufacturing defects.

- Minimum steel yield strength shall be 355 MPa.

Corrosion Protection

- All fabricated steel members shall be Hot Dip Galvanized after fabrication.

- Galvanizing shall comply with ISO 1461.

- Minimum coating thickness shall be 70 μm.

- Galvanized surfaces shall be free from rust, cracks, peeling, bare patches and other defects.

    - Foundation Specification

- Foundations shall be constructed as detailed in the Tender Drawings and verified by the Contractor's structural calculations.

- The standard foundation arrangement shall comprise:

  - Circular Reinforced Concrete Pile Foundation

  - Diameter: 400 mm

  - Depth Below Ground Level: 1600 mm

  - Pedestal Projection Above Ground Level: 150 mm

  - Concrete Grade: C25/30 Minimum

- Each central column shall be securely fixed to the concrete foundation through galvanized base plates and anchor systems designed for the applicable uplift and overturning forces.

- Foundation dimensions shown in the Tender Drawings shall be verified by the Contractor and adjusted if required based on site geotechnical conditions and structural design calculations.

    - Fabrication

- All members shown in the Tender Drawings shall be CNC punched and CNC cut in the factory.

- All holes shall be pre-engineered and match the selected 650Wp module dimensions.

- All structural members shall be fabricated from cold-formed galvanized C-channel sections.

- All fabrication activities including cutting, punching, drilling and fitting shall be completed prior to galvanizing.

- No site drilling, cutting, welding, punching or modification shall be permitted.

- All members shall be clearly marked to correspond with the approved assembly drawings.

    - Connections

- Connections between the central column, rafters, purlins and bracing members shall be bolted as detailed in the Tender Drawings and approved shop drawings.

- Structural bolts shall be M10 Stainless Steel Grade SS304 complete with nuts, flat washers and spring washers.

- PV module fixing bolts shall be M8 Stainless Steel Anti-Theft Type complete with nuts and washers.

- Connection cleats and brackets shall be fabricated from galvanized structural steel compatible with the connected C-channel members.

- All bolts shall be mechanically tightened to the manufacturer's specified torque.

- The length of bolts shall permit a minimum projection of two threads and maximum projection of five threads beyond the nut after tightening.

- All fasteners shall be stainless steel and suitable for long-term outdoor service in corrosive environments.

    - Bidder's Technical Proposal Submission Requirements

The Bidder shall submit a comprehensive technical proposal demonstrating compliance of the proposed Module Mounting Structure (MMS) with the requirements of the specification. The submission shall include a general description of the proposed mounting system, preliminary structural concept and layout, typical drawings, material specifications, design assumptions, and evidence of compliance with the specified wind load, structural stability, durability, and design life requirements. The Bidder shall also provide product datasheets, material certificates, quality assurance procedures, proposed fabrication and installation methodology, warranty information, and details of previous similar project experience. The technical proposal shall clearly demonstrate that the proposed MMS is suitable for the intended application and can be delivered, installed, and operated in accordance with the project requirements.

  - WELDED MESH FENCING SYSTEM

    - Scope of Work

The fencing system comprises three major elements: Welded mesh panels; Steel posts (Line, corner, End, Struts posts); Fittings (Clamps with screws/bolts); Concrete (for embedded posts),  and optional perimeter curbs), and Anti-rust primer and touch-up paint..

The Contractor shall provide all labor, supervision, materials, tools, equipment, transportation, testing, documentation, and incidentals required for the complete supply, fabrication, delivery, installation, testing, and commissioning of the Welded Mesh Security Fencing System suitable for Solar PV Arrays.

The work covers supply, providing & fixing of welded mesh Fencing as per attached shop drawings. Fencing shall be erected to a smooth alignment with no abrupt irregularities. The ground shall be trimmed or filled in such a manner that the bottom of the fence will approximately follow the level of the ground. The distance between the bottom of welded mesh and hoardings and the ground shall not exceed 100 mm and any gap between the bottom of hoardings and the ground shall be sealed to the satisfaction of the Engineer.

The work shall include, but not be limited to:

- Supply all materials required for the fencing work including Welded mesh fence panels, Posts with post caps, Pedestrian gates and Vehicle access gates, Connection lugs. Anti-theft fasteners, Bolts, nuts and washers, Concrete and forms materials, Paints and coatings, and all accessories are required for complete installation

- The Contractor shall Fabricate steel posts and gates. Install fence posts plumb and aligned. Erect welded mesh panels. Install straining and corner supports. Install all gates complete with hardware. Apply corrosion protection and finishes. Repair any damaged coating after installation.

- The Contractor shall: Set out the fence alignment, use stakes and string line to mark the straight path where fencing will be installed. Clear vegetation, shrubs and debris along the fence route. Remove obstructions affecting fence installation.

- The Contractor shall excavate all post foundations. Excavate trench for concrete curb. Dispose surplus excavated materials.

- Cast all concrete foundations c25 grade minimum for posts and concrete perimeter curbs as specified. Cure all concrete work for at least 48hours

- The contractor shall Supply, construct, test and complete continuous plain concrete curb beneath the welded mesh security fence. The work includes setting out, excavation, trimming, formwork, concrete supply and placement, compaction, curing, backfilling, disposal of surplus excavated material, construction joints, finishing and all labor, materials, equipment, tools and incidentals required for a complete installation in accordance with the approved drawings and specifications.

- Finishing touch

              - Paint Touch-Up: Apply zinc-rich or epoxy primer on scratches or cut areas.

- Clean Up: Remove excess concrete and clear debris

- Final Inspection: Ensure the fence is aligned, stable, and free of loose parts.

    - MATERIAL SPECIFICATION

- Mesh Panels

- Dimensions: 2.2m height x 2.5m wide, Wire: 4.0 mm diameter

- Gid opening: 50 mm × 150 mm

- Base steel Material: Q195 steel, electrically welded mesh

- Reinforcement: two to three horizontal V-bends.

- Coating System: Hot Dip Galvanizing, Minimum zinc: 60 μm.

- Powder Coating: PVC or Polyester powder or, Minimum 80 μm.

- Standard Colour: Light Blue (RAL 5012).

- Certifications: ASTM, ISO9001, RoHS, CE, and SGS or equivalent.

- Steel posts

- Base Material: Q235 Structural Steel.

- Post size: SHS 60 × 60 × 2 mm, Length total =3m

- Finish: Hot dip galvanized + Light Blue Polyester powder coated

- Provided with UV resistant plastic cap; or Pressed steel cap.

- Caps shall be weatherproof and securely fixed.

- Fittings

The system shall use rigid 40x50mm metal clips to secure the welded steel mesh panels. These fittings are bolted every 400mm using 8mm diameter round head bolts.

- Minimum bolt grade: 4.6.; Hot-dip galvanized finish.

- Each post shall include: 10 connection lugs, 5 on each side

- Post Foundation

Concrete shall be cast directly around the posts and Posts shall be centrally positioned and vertically aligned.

- Concrete C25 Grade minimum

- Dimensions: 350 mm × 350 mm × 800 mm

- Gate system

- Type 1 Gate – Single leaf (1 x 1m, 1m wide)

- Dimensions: Clear opening width = 1.0 m; Height = 2.2 m

- Gate Frame: RHS 30 × 50 × 1.2 mm

- Gate Posts: SHS 100 × 100 × 4 mm

- Gate Infill: Same welded mesh as fence

- Finish: Hot dip galvanized + Light Blue Polyester powder coated

- Hardware: Heavy-duty hinges. Lockable latch. Padlock provision. Stop plate.

- Type 2 Gate – Double leaf (2 x 1.5, 3m wide)

- Dimensions: Clear opening width = 3.0 m; Height = 2.2 m

- Gate Frame: RHS 30 × 50 × 1.2 mm

- Gate Posts: SHS 100 × 100 × 4 mm

- Bracing: Angle L50 × 50 × 5 mm

- Gate Infill: Same welded mesh as fence

- Finish: Hot dip galvanized + Light Blue Polyester powder coated

- Hardware: Heavy-duty hinges. Lockable latch. Padlock provision. Stop plate.

- Gate Foundations:

- Reinforced concrete Grade C25/20.

- Minimum size 400 × 400 × 800 mm.

- Concrete Curb

- construction along the perimeter fence

- Dimensions: Width = 200 mm, Depth = 300 mm,

- Constructed from Plain concrete Grade: C25,

    - Measurement method

The Contractor shall submit detailed unit rates all as per technical specifications for:

- Complete Welded Mesh panels with accessories (Unit: No.)

- RHS posts with lugs bolts and accessories (Unit: No.)

- C25 concrete footings including pit excavation and backfilling;(No)

- Type-1 Pedestrian Gates including gate posts, infill, frames, (Unit: No.);

- Type-2 Vehicle Gates (Unit: No.);

- Concrete Curb (Unit: Linear Meter).

- Summary BOQ of Fence Work (Refer to attachment table 2.1C)

| SN | DESCREPTION | TOTAL QTY | UNIT |
| --- | --- | --- | --- |
| 1 | RHS Posts w/ lugs 3m | 1066 | pcs |
| 2 | C25 concrete footing | 45 | m3 |
| 3 | Welded Mesh panel, 2.5m | 1041 | pcs |
| 4 | C25 concrete base Curbs | 156 | m3 |
| 5 | Type 1 Gate 1m complete | 25 | No. |
| 6 | Type 2 Gate 3m complete | 12 | No. |

  - MANHOLES, AND VALVE CHAMBERS,

    - Manhole

Supply, construct, and install a Manhole with the following specifications: The work includes excavation in any type of soil to any depth, backfilling with clean sand and compaction

- Size: 70 x 70 cm

- Material: Solid concrete blocks 15 x 20 x 40 cm

- Watertight and airtight

- Base: At least 15 cm thick of cast in situ concrete

- Plastering: Yes

- Painting: Two coats of hot bituminous paint

- PVC cover: Yes, can withstand 200 kg/m²

All work to be completed as per specifications drawings & to the complete satisfaction of the supervisor engineer

    - Valve Chambers

Supply and install a valve chamber as per specifications and drawing: The work includes excavation in any type of soil to any depth, backfilling with clean sand and compaction

- Size: 120x60x60cm minimum

- 15cm solid concrete block Wall

- plastered and painted both internal & external

- C.S cover, Minimum plate thickness 3mm;

- Angle frame 50x50x5mm, painted two layers, anti-corrosion and enamel

- Drainage PVC pipe 1 inch in the lower level

  - CONCRETE BASEMENT FOR PUMP AND GENSET

Concrete Basement for Pumps and Generators shall be constructed:

- On a level, reinforced concrete plinth. Cast outside in open area - RCC foundation B300kg/cm2.

- Reinforcement shall be 420 MPa and a rebar diameter of 12mm @ 20cm as specified in the design.

- The height of this foundation should be 300mm above ground level, or as recommended by the generator/Pump set manufacturer, whichever is greater.

- Sizing depending on each supplied pump, and genset dim + manufacturer recommended margins. The foundation's length and breadth must be at least 250mm greater on all sides than the enclosure's dimensions.

- The price includes all necessary basaltic hardcore filling (250mm min.), excavation and compaction works to prevent settlement and to achieve the required soil bearing capacity.

- Surface Finish: Smooth trowel finish with anti-slip surface.

- Anchor Bolts: Provided for fastening equipment.

- Drainage: Adequate slope and drainage channels to prevent water accumulation.

  - TRENCHES FOR PIPELINE INSTALLATIONS

- General

The contractor shall carry out all civil works required for the installation, testing, commissioning, and reinstatement of water supply pipelines and appurtenances.

The scope shall include, but not be limited to:

Route surveying and setting out, Site clearance; Excavation of trenches; Dewatering where required; Disposal of surplus excavated materials; Trench bedding preparation; Pipe laying and alignment; Selected backfill placement; Trench backfilling and compaction; Concrete anchor blocks; Concrete thrust blocks; Valve chambers; Air valve chambers; Drain valve chambers; Fire hydrant support blocks; Protection works at road crossings; Testing and commissioning support; Environmental protection measures; Traffic management where required, and Cleaning and restoration of work areas

- Trench Excavation, and Backfilling

Excavation shall be carried out to the required depth, width, and alignment. Stable side slopes. Trench shoring where required. Protection of adjacent utilities. Removal of unsuitable materials.

- Trench dimensions

| Minimum Trench Width |  | Minimum Trench Depth/Cover |  |
| --- | --- | --- | --- |
| Pipe Diameter | Recommended Trench Width | Location | Minimum Cover |
| DN20-DN100 | Pipe OD + 300 mm | Open Ground | 0.80 m |
| DN150-DN300 | Pipe OD + 400 mm | Roads | 1.00 m |
| DN350-DN600 | Pipe OD + 600 mm | Major Roads | 1.20 m |

- Pipe Bedding:

- Bedding Material shall consist of: Sand; Fine granular material; Imported selected fill

- Bedding Thickness:

- Bedding Material shall be: 100 mm for uPVC/HDPE pipes, 150mm for DCI pipes

- Requirements: Uniform support along pipe length. Free from stones larger than 20 mm.; Free from organic matter.

- Pipe Surround and Initial Backfill

- Initial backfill shall: Extend at least 300 mm above pipe crown. Consist of selected granular material. Be free from rocks and debris.

- Compaction: Minimum compaction 95% Modified Proctor Density

- Final backfill shall: Use approved excavated material or imported fill. Be placed in layers not exceeding 200 mm. Be compacted to specified density.

- Concrete Works for thrust and

- Thrust Blocks

Concrete thrust blocks shall be provided at: Bends; Tees; Reducers; Dead ends; Valves where required

Concrete Grade: C25 minimum

Design Based on: Pipe diameter; Operating pressure; Soil bearing capacity

- Anchor Blocks

Anchor blocks shall be provided on: Steep slopes; Vertical bends; Exposed sections; Special crossings

Concrete Grade: C25 minimum

- Pipe Supports

Where exposed pipework exists:

- Reinforced concrete support shall be provided.

- Supports shall prevent sagging and movement.

- Quality Requirements

| Item | Requirement |
| --- | --- |
| Cement | ASTM C150 / EN 197 |
| Aggregate | ASTM C33 |
| Reinforcement | ASTM A615 Grade 60 or Equivalent |
| Sand | Clean, well graded |
| Water | Clean and potable |
| Blocks | Minimum 7 MPa compressive strength |

  - OVERHEAD TRAVELLING CRANE SYSTEMS

- General

The Contractor shall design, supply, fabricate, deliver, install, test and commission complete overhead travelling crane systems for lifting and handling pumps, motors, generators and associated equipment at pumping stations, control rooms and utility facilities.

The overhead crane system Components includes:

- Electric Hoist with Manual Override Capability

Complete lifting unit comprising electric motor, gearbox, load chain or wire rope, hook block with safety latch, electromagnetic brake, overload protection, upper and lower limit switches, control pendant and manual override mechanism for emergency operation during power failure.

Requirement: Safe working load Capacity shall be 2-, 4-, and 6-ton Electric Hoist

- Material requirements

- Fabricated steel construction.

- Alloy steel Grade 80 minimum load chain.

- High-strength steel wire rope where applicable.

- Forged alloy steel hook with safety latch.

- Hardened alloy steel gears.

- Electromagnetic fail-safe brake.

- Protection class IP55 minimum.

- Manual Push Trolley Assembly

Beam-mounted trolley designed to support and carry the hoist consisting of trolley frame, wheels, bearings, adjustable suspension arrangement, anti-drop device and all necessary hardware.

Requirements:

- Capacity equal to crane Safe working Load(SWL); Adjustable to beam flange width; and Smooth manual operation.

Material:

- Fabricated steel side plates.

- Forged or cast steel wheels.

- Carbon steel axles.

- Sealed anti-friction bearings.

- Corrosion-protected finish.

- Single-Girder Bridge Crane with Manual Push Travel

Structural steel bridge girder complete with end carriages, wheel assemblies, manual bridge travel system, end stops and accessories required for crane travel along runway beams.

Requirements:

Manual bridge travel; Maximum deflection L/750; and designed for SWL plus impact loading

Materials

- Structural steel S275 or S355.

- EN 10025 compliant.

- ASTM A36/A572 equivalent acceptable.

- Forged steel wheels.

- Heavy-duty bearings.

- Runway Beams and Supporting Steelwork

Two parallel runway beams complete with support columns, wall brackets, bracing, base plates, connection plates, anchorages, End stops, U-bolts and Miscellaneous steelwork.

Materials

- Structural steel S275/S355 minimum.

- Fasteners Grade 8.8 minimum.

- Hot-dip galvanized or epoxy coated.

- Reinforced Concrete Foundations

Reinforced concrete foundations supporting the crane structure including excavation, reinforcement, concrete placement and anchor bolt installation.

- Concrete Grade C30 minimum; Reinforcement steel fy = 460 MPa minimum.

- Hot-dip galvanized anchor bolts; Minimum anchor bolt size M24.

- Corrosion protection

- Hot-Dip Galvanizing: Minimum zinc coating thickness 85 microns.

- Coating System: Zinc-rich epoxy primer. Polyurethane top coat.

- Minimum DFT: 250 microns.

- Testing and commissioning

Functional Testing to verify: Hoist operation. Brake operation. Trolley travel. Bridge travel. Limit switches. Safety devices. The Contractor shall provide a load testing certificate prior to handover.

Proof Load Testing:

| Crane SWL | 2 Ton | 4 Ton | 6 Ton |
| --- | --- | --- | --- |
| Proof Load | 2.5 Ton | 5.0 Ton | 7.5 Ton |

- Applicable standards

The crane system shall comply with the latest editions of: EN 15011 – Bridge and Gantry Cranes; ISO 4301 – Crane Classification; ISO 9927 – Crane Inspection; FEM Rules for Hoisting Equipment; EN 10025 – Structural Steel; Applicable local building codes; Applicable occupational health and safety regulations

  - VISIBILITY SIGNPOST

- General

The Contractor shall be responsible for the design verification, supply, fabrication, transportation, installation, and commissioning of a complete double-sided project identification signboard for the Solar PV Water Supply System. The signboard shall be suitable for outdoor installation and constructed using hot-dip galvanized steel support members, Aluminum Composite Panel (ACP) sign faces, reinforced concrete foundations, and durable weather-resistant graphics.

The completed signboard shall be structurally stable, corrosion-resistant, legible, and capable of withstanding normal environmental conditions, including wind, rainfall, solar radiation, dust, and temperature variations prevalent at the project location. The Contractor shall deliver the signboard as a fully functional, complete, and approved installation, including all incidental works necessary for its satisfactory operation and long-term durability.

- Technical requirements

The contractor shall provide, transport, fabricate, paint, and install a complete double-sided project signboard for Solar PV Pumping Systems.

| - Dimensions | - Sign face: 2.0 m (W) × 1.0 m (H) - Overall height: approximately 2.6 m above finished ground level - Double-sided display |
| --- | --- |
| - Frame | - Posts: SHS steel section 60 × 60 × 3 mm, 2 Nos. - Perimeter frame: SHS steel section 60 × 60 × 3 mm. - All joints fully welded and ground smooth. |
| - Sign Face | - 3 mm Aluminum Composite Panel (ACP), double-sided; or approved equivalent. - UV-resistant printed and laminated graphics. - Project information in English and local language. - UNICEF/Government/Donor logos as approved by the Client. |
| - Protection | - All steel members hot-dip galvanized after fabrication. - Minimum zinc coating: 85 microns. - Finish coat: Two coats exterior-grade polyurethane paint, RAL 5012 (Light Blue) or approved equivalent. |
| - Foundation | - Reinforced concrete footing for each post. - Minimum footing size: 500 × 500 × 700 mm deep. - Concrete grade: C25/30. - Including excavation, backfilling and site reinstatement. |
| - Fasteners | - M12 galvanized anchor bolts with nuts and washers. - All exposed fasteners corrosion resistant. |
| - Workmanship | - Signboard shall be plumb, level and securely fixed. - Drainage holes provided in hollow sections. - Designed to withstand normal site wind loads and outdoor environmental conditions. - Complete installation including all labor, transport, tools, materials, concrete works, painting, graphics and commissioning. |
| - Design Life | - Structural life: minimum 15 years. - Corrosion protection life: minimum 10 years before major maintenance. |

# SCADA AND REMOTE MONITORING SYSTEMS

  - SCOPE OF WORK

UNICEF supports the development, rehabilitation, and operation of rural and urban water supply systems across Ethiopia, including hybrid solar photovoltaic (PV) powered water pumping systems, generator-assisted schemes, and grid-connected installations. To improve operational efficiency, system reliability, energy management, water production monitoring, and timely maintenance interventions, UNICEF intends to the provision of Supervisory Control and Data Acquisition (SCADA), telemetry, remote monitoring, and intelligent control solutions.

The LTA shall provide a standardized and scalable platform capable of monitoring and managing multiple water supply facilities distributed across different geographical locations through a centralized cloud-based monitoring system. The solution shall support both newly constructed facilities and existing water schemes requiring integration into a unified monitoring platform.

The proposed system shall provide real-time and historical monitoring of water production, solar energy generation, pumping performance, reservoir levels, generator operation, grid power availability, and other critical operational parameters while enabling proactive maintenance and performance management. The solution shall support remote monitoring and, where authorized, remote control of hybrid solar water pumping systems with individual pump capacities of 7.5 kW and above or as specified under individual call-off contracts.

The Contractor shall provide a complete SCADA and Remote Monitoring Solution including all engineering, software, hardware, instrumentation, communications, installation, commissioning, training, warranty, and support services necessary for reliable operation.

The scope shall include, but not be limited to:

- Site survey, assessment, and detailed engineering design;

- SCADA software, cloud hosting, web-based dashboards, GIS interface, database services, mobile application access, reporting, and analytics tools;

- RTUs, PLCs, data loggers, communication gateways, industrial routers, antennas, power supplies, batteries, surge protection devices, enclosures, switches, and associated field equipment;

- Supply, installation, calibration, and integration of sensors and instrumentation including flow meters, water level sensors, pressure transmitters, electrical energy meters, solar irradiance sensors, fuel level monitoring devices, and other monitoring devices required by the project;

- Integration of solar PV systems, solar pump inverters, hybrid inverters, pumps, motors, VFDs, soft starters, generator systems, utility grid systems, electrical protection devices, and associated equipment;

- Real-time monitoring of solar performance, water production, pump operation, electrical parameters, reservoir levels, generator operation, grid availability, and system alarms;

- Remote monitoring and remote control functions where specified;

- Data acquisition, local data storage, buffering, synchronization, historical archiving, and secure data transmission;

- User management, cybersecurity controls, encrypted communications, VPN access, audit trails, and secure cloud hosting;

- Alarm management including SMS, email, and mobile application notifications;

- Dashboard configuration, GIS mapping, KPI calculations, performance analytics, trending, reporting, and data export functionality;

- Factory Acceptance Testing (FAT), Site Acceptance Testing (SAT), calibration, validation, performance verification, commissioning, and system handover;

- Operator and maintenance training, operation and maintenance manuals, as-built drawings, configuration backups, and project documentation;

- Twenty-four (24) months warranty, software updates, cybersecurity patches, remote technical support, and warranty services.

The Contractor shall provide all equipment, software, licenses, interfaces, accessories, communication devices, wiring, mounting hardware, power supplies, integration services, engineering services, testing equipment, documentation, and ancillary works necessary to deliver a complete, operational, tested, commissioned, and fully integrated SCADA and Remote Monitoring System.

Any item required for proper operation, safety, performance, interoperability, communication, monitoring, control, cybersecurity, testing, commissioning, or reliability of the system, whether specifically identified in the BOQ or not, shall be deemed included in the Contractor's rates.

  - SYSTEM ARCHITECTURE

The SCADA system shall consist of:

- Site Level Equipment

Each pumping station shall include: RTU/Data Logger; Communication gateway; Local data storage; Monitoring sensors; Auxiliary power supply; Protection devices; Secure enclosure.

- Central Monitoring Platform

- The central platform shall include: Cloud-hosted dashboard; GIS-based monitoring interface; Historical database; Alarm management tools; Reporting tools; User management platform; Mobile application.

- Multiple pumping stations shall be capable of reporting to a single centralized dashboard.

  - MINIMUM MONITORING REQUIREMENTS

- Solar PV Monitoring

The system shall monitor and record:

- PV Array Voltage; PV Array Current; PV Array Power; Solar Operating Hours

- Daily Solar Energy Yield; Cumulative Solar Energy; Inverter Efficiency

- Solar Irradiance (where applicable); Solar Irradiance (where applicable)

- Pump Monitoring

The system shall monitor:

- Pump Status (Run/Stop/Fault, Fault Codes),

- Motor Voltage; Motor Current; Motor Power; Frequency

- Running Hours, Number of Starts, Pump Efficiency,

- Water System Monitoring

- Instantaneous Flow Rate; Daily Water Production; Total Water Production

- Borehole Dynamic Water Level; Borehole Static Water Level

- Reservoir Water Level; Tank Level Percentage

- Generator Monitoring

- Where generators are installed:

- Generator Status; Fuel Level; Fuel Consumption

- Generator: Voltage, Current, Power, Energy Production, Running Hours

- Grid Monitoring

Where grid power exists:

- Grid Availability, Voltage, Current, Frequency, Imported Energy, Outage Records

  - DATA LOGGER / RTU REQUIREMENTS

Minimum Specification

| Enclosure | IP65 Minimum |
| --- | --- |
| Operating Temperature | -20°C to +70°C |
| Data Storage | 12 Months Minimum |
| Communication Ports | RS485, Ethernet, USB |
| Protocols | Modbus RTU, Modbus TCP/IP |
| Power Supply | 12/24VDC |
| Backup Autonomy | 72 Hours Minimum |
| Logging Interval | 1 to 60 Minutes Adjustable |

The RTU shall automatically store data during communication failures and synchronize data upon communication restoration.

  - SENSORS AND INSTRUMENTATION

the SCADA system shall be capable of integrating both existing and newly supplied sensors and instrumentation.

Where suitable and functional sensors, meters, transmitters, and monitoring devices already exist at the site, the Contractor shall integrate them into the SCADA system through compatible communication protocols and interfaces.

Where existing instrumentation is unavailable, incompatible, defective, obsolete, or insufficient to achieve the required monitoring functionality, the Contractor shall supply, install, calibrate, and commission new sensors and instrumentation.

| Flow Meter | - Electromagnetic or Ultrasonic. - Accuracy: ±2% or better. - Output: Pulse, 4–20mA or Modbus. |
| --- | --- |
| Water Level Sensor | - Pressure Transducer or Ultrasonic. - Accuracy: ±0.5%. - Protection: IP68. |
| Irradiance Sensor (Optional) | - Pyranometer. - Range: 0–1500 W/m². - ISO-compliant. |
| Electrical Meters | - Class 1 Accuracy or better. - Measurement of: Voltage; Current; Power; Power Factor; Frequency; Energy. |

    - COMMUNICATION REQUIREMENTS

The system shall support:

- GSM/GPRS; 3G; 4G/LTE; NB-IoT; LoRaWAN; Ethernet;

- Satellite communications where required

Minimum Requirements

- Automatic reconnection; Data buffering; VPN-compatible;

- High-gain antenna; Dual SIM capability preferred.

Communication availability shall be at least 99%, subject to network coverage.

    - SOFTWARE PLATFORM REQUIREMENTS

The platform shall provide:

- Real-Time Dashboard: -Station overview; Equipment status; Water production; Solar production; Active alarms; GIS map display.

- Historical Data:- Data trending; Downloadable reports; Data export (Excel, CSV, PDF).

- Analytics: - Specific Energy Consumption (kWh/m³); Solar Contribution (%); Pump Efficiency; Water Production; Energy Savings; System Availability.

    - ALARM MANAGEMENT

The SCADA platform shall generate alarms for:

- Pump fault; Dry running; Tank overflow; Tank low level;

- Generator fault; Communication loss;

- Inverter fault; Over-current; Over-voltage; Low solar production;

- Intrusion alarm where applicable.

Notifications shall be available through:

- SMS; Email; Mobile App notification.

    - CYBERSECURITY REQUIREMENTS

The system shall provide:

- User authentication; Password protection; Role-based access;

- Encrypted communication; Audit trail; Remote device management; Secure cloud hosting.

All operational data shall remain the property of UNICEF and/or the responsible utility.

  - TESTING AND COMMISSIONING

    - TESTING

The Contractor shall perform all testing, calibration, commissioning, and performance verification activities necessary to demonstrate that the SCADA and Remote Monitoring System is fully functional, integrated, reliable, and compliant with the Contract requirements.

Testing and commissioning shall cover all field equipment, sensors, RTUs/PLCs, communication systems, cloud platform, dashboards, reporting functions, alarms, mobile applications, and integrated third-party devices.

- Factory Acceptance Test (FAT)

Prior to shipment and installation, the Contractor shall conduct Factory Acceptance Testing to verify hardware functionality, software configuration, communication interfaces, alarm functions, database operation, and dashboard performance.

A FAT report shall be submitted for review.

- Site Acceptance Test (SAT):

Upon completion of installation, the Contractor shall conduct Site Acceptance Testing (SAT) in the presence of UNICEF and/or the designated Client representative. A SAT report shall be submitted as part of the commissioning documentation.

    - PERFORMANCE ACCEPTANCE CRITERIA

The system shall satisfy the following minimum requirements:

- All specified monitoring points operational and reporting correctly.

- Communication availability of at least 99% (subject to network coverage).

- Automatic data buffering during communication failures.

- Automatic synchronization of stored data after communication restoration.

- Alarm notifications transmitted successfully.

- Historical data logging functioning correctly.

- Mobile and web-based dashboards fully operational.

- All FAT and SAT requirements successfully completed.

    - COMMISSIONING AND HANDOVER

Final acceptance shall be subject to:

- Successful completion of FAT and SAT;

- Submission of commissioning reports and calibration certificates;

- Delivery of as-built drawings and O&M manuals;

- Completion of operator training;

- Resolution of all critical defects and punch-list items.

The system shall be considered commissioned only after demonstrating stable and reliable operation under normal operating conditions and receiving formal acceptance from UNICEF or the designated Client representative.

  - PROCUREMENT TENDER NOTE

The Contractor's rates for each BOQ item shall include design, engineering, procurement, supply, software licenses, cloud services, field equipment, communication equipment, sensors and instrumentation, installation materials, programming, integration, testing, commissioning, documentation, training, warranty obligations, technical support, and all ancillary items necessary for complete and reliable operation of the SCADA and Remote Monitoring System.

The rates shall cover, as applicable:

- Site surveys and assessments and design;

- RTUs, PLCs, data loggers, communication gateways, routers, and associated hardware;

- Supply, installation, calibration, and commissioning of sensors and instrumentation;

- Communication equipment, SIM configuration, network setup, and cybersecurity services;

- Cloud hosting, software licensing, database management, and mobile application access;

- SCADA configuration, dashboard development, reporting, analytics, and alarm management;

- Integration with solar PV systems, pumps, VFDs, generators, grid systems, and other associated equipment;

- Factory Acceptance Testing (FAT), Site Acceptance Testing (SAT), performance testing, and commissioning;

- Training, operation and maintenance manuals, and as-built documentation;

- Warranty services, software updates, security patches, and technical support.

Any component, interface, accessory, software module, communication device, sensor, instrument, engineering service, or ancillary item required for proper system functionality shall be deemed included within the relevant BOQ rates whether specifically listed or not.

No additional payment shall be made for items reasonably required to deliver a complete, operational, tested, commissioned, and fully integrated SCADA and Remote Monitoring System.

BOQ Description

Supply, deliver, install, configure, program, integrate, test, commission, document, train, warrant, and support a complete SCADA, Telemetry, and Remote Monitoring System for Hybrid Solar PV Water Pumping Systems, including all hardware, software, communication infrastructure, sensors, instrumentation, cloud services, and ancillary components required for reliable operation.

The system shall provide centralized monitoring, data acquisition, alarm management, reporting, analytics, and remote access for solar-powered, grid-connected, generator-supported, and hybrid water pumping systems. The solution shall support monitoring of one or multiple geographically dispersed pumping stations through a single centralized monitoring platform.

# RECOMMENDED AND MANDATORY SPARE PARTS

  - GENERAL

For an O&M-focused LTA, the spare parts schedule should primarily consist of failure-prone maintenance components. These Parts are components that deteriorate during normal operation and are expected to be periodically replaced due to friction, abrasion, corrosion, pressure cycling, electrical stress, aging, UV exposure, or chemical attack.

The purpose of the spare parts supply is to ensure continuous operation, preventive maintenance, corrective maintenance, and minimization of downtime during the operational life of the systems.

The Contractor shall supply, deliver, label, package, document, and support the provision of operation and maintenance (O&M) spare parts for all equipment supplied under the Long-Term Arrangement (LTA) for Hybrid Solar PV Water Pumping Systems and associated infrastructure.

The Contractor shall provide unit rates and supply spare parts on an as-requested basis through Call-Off Orders issued under the LTA.

The Contractor shall provide spare parts under the following categories:

Exclusions: A replacement of items, example  Complete pumps, Complete generators, etc, shall not be considered routine spare parts and shall not form part of the standard spare parts schedule unless specifically requested in the Call-Off Contract. These items shall be treated as replacement equipment and procured separately.

- Spare Parts Categories

The Contractor shall provide spare parts under the following categories:

| Category A: Pumps and Motors | Including: Impellers; Diffusers; Bearings; Mechanical seals; Wear rings; Coupling inserts; Cable gland kits; Pump repair kits |
| --- | --- |
| Category B: Pump Inverters (VFD) | Including: Control PCB boards; Communication cards; HMI displays; Cooling fans; DC capacitors; Fuse kits; Terminal connectors |
| Category C: Solar PV Systems | Including:MC4 connectors; Fusion connectors; DC fuses;Fuse holders; SPD cartridges; Junction box components; Earthing clamps; Cable glands |
| Category D: Battery Systems (BESS) | Including: Battery fuse kits; Cooling fans; Communication modules; Temperature sensors; Contact sets; DC disconnect accessory kits |
| Category E: Diesel Generator set | Including: Fuel filters; Oil filters; Air filters; V-belts; Solenoid valves; Temperature sensors; Oil pressure sensors; AVR modules; Battery charger modules |
| Category F: Grid Connection Systems | Including: MCBs; Protection fuses; Contactors; relays; SPD cartridges; Indicator lamps; Selector switches; Terminal blocks |
| Category G: SCADA and Telemetry Systems | Including: modems; Antennas; modules; Memory cards; UPS batteries; Flow sensors; Pressure sensors; Water level sensor |
| Category H: Water Treatment Systems | Including: Dosing pump diaphragms; Injection valves; Tubing kits; O-ring kits; Filter nozzles; Solenoid coils; Pressure gauges; UV lamps; Quartz sleeves; Chlorine sensors |
| Category I: Valves, and Fittings Systems | Including: Valve seat kits; Stem packing kits; O-ring kits; Gasket kits; Coupling seals; Repair clamps; Electrofusion accessories |

- Supply and Delivery Requirements

The Contractor shall:

- Provide genuine OEM spare parts.

- Ensure full compatibility with supplied equipment.

- Deliver spare parts within the timelines specified in the LTA or Call-Off Contract.

- Supply manufacturer part numbers.

- Supply installation and replacement instructions where applicable.

- Clearly label all spare parts.

- Documentation Requirements

The Contractor shall provide:

- Spare parts catalogue

- Manufacturer part numbers

- Recommended replacement intervals

- Storage instructions

- Warranty information

- Illustrated spare parts lists

- Traceability records

- Availability and Supply Support

The Contractor shall guarantee the availability of spare parts for a minimum period of ten (10) years after equipment supply. The Contractor shall maintain sufficient stock or supply arrangements to ensure timely delivery of critical spare parts.

- Warranty

All supplied spare parts shall be covered by a minimum twelve (12) month warranty against manufacturing defects and material failures.

- Spare parts rate schedule

NOTE to Bidders

- Prices shall be quoted in the currency specified in the tender.

- Rates shall include supply, packaging, transport, handling, duties, and delivery.

- All spare parts shall be genuine OEM parts compatible with the offered equipment.

- Rates shall remain fixed throughout the LTA period.

- Spare parts shall be supplied upon request through individual Call-Off Orders.

- Only operation and maintenance spare parts shall be included.

# ATTACHMENT:

# Attachement-1: Bidder’s Technical Compliance Form

- MOTOR-PUMP UNIT (SUBMERSIBLE AND SURFACE PUMPS)

- GENERAL COMPLIANCE REQUIREMENTS

| No. | Requirement | Offered | (C/PC/NC) | Evidence |
| --- | --- | --- | --- | --- |
|  | Suitable for Solar Water Pumping Systems |  |  |  |
|  | Compatible with AC output from Solar Pump VFD |  |  |  |
|  | Supply, Install, Test & Commission Included |  |  |  |
|  | Meets applicable performance schedule |  |  |  |
|  | Complete technical documentation submitted |  |  |  |
|  | Minimum as specified |  |  |  |

- PERFORMANCE SCHEDULE COMPLIANCE

B1. Applicable Motor Rating

| Ref. No. | Item | Requirement | Offered |
| --- | --- | --- | --- |
|  | Motor Rating (kW) |  |  |
|  | Flow Range (m³/hr) |  |  |
|  | TDH Range (m) |  |  |
|  | Pump Curve Reference |  |  |

B2. Performance Envelope Verification

| No. | Requirement | Offered | C/PC/NC | Evidence |
| --- | --- | --- | --- | --- |
|  | Certified Pump Curve Submitted |  |  |  |
|  | Hydraulic Datasheet Submitted |  |  |  |
|  | Motor Datasheet Submitted |  |  |  |
|  | Pump Selection Report Submitted |  |  |  |
|  | Efficiency Curve Submitted |  |  |  |
|  | Full Flow Range Covered |  |  |  |
|  | Full TDH Range Covered |  |  |  |
|  | Motor Rating Not Exceeded |  |  |  |
|  | Pump Operates Within POR |  |  |  |
|  | Low Head Duty Covered |  |  |  |
|  | Medium Head Duty Covered |  |  |  |
|  | High Head Duty Covered |  |  |  |

- PUMP REQUIREMENTS

C1. Pump Construction

| No. | Requirement | Offered | C/PC/NC | Evidence |
| --- | --- | --- | --- | --- |
|  | Type: Multistage Mixed/Radial Flow |  |  |  |
|  | Pump Casing AISI 304 SS or Better |  |  |  |
|  | Impeller AISI 304 SS or Better |  |  |  |
|  | Diffuser AISI 304 SS or Better |  |  |  |
|  | Shaft AISI 304 SS or Better |  |  |  |
|  | Fasteners Stainless Steel |  |  |  |
|  | NEMA Coupling Compliant |  |  |  |
|  | Sand Content≤100 g/m³ |  |  |  |
|  | BH Clearance≥40 mm |  |  |  |

C2. MOTOR REQUIREMENTS

| No. | Requirement | Offered | C/PC/NC | Evidence |
| --- | --- | --- | --- | --- |
|  | Type Three Phase AC |  |  |  |
|  | Voltage380-400 VAC |  |  |  |
|  | Frequency50 Hz |  |  |  |
|  | Rewindable |  |  |  |
|  | VFD Compatible |  |  |  |
|  | Insulation Class Class F or Better |  |  |  |
|  | Protection Rating IP68 Minimum |  |  |  |
|  | Water Temperature Up to 45°C |  |  |  |
|  | Efficiency ≤7.5kW, ≥80% |  |  |  |
|  | Efficiency >7.5kW, ≥85% |  |  |  |
|  | Mechanical Seal, Tungsten Carbide/Ceramic |  |  |  |
|  | Radial Bearing Graphite or better |  |  |  |
|  | Thrust Bearing Graphite & SS Pads or Better |  |  |  |
|  | Submersible Cable Included |  |  |  |
|  | Cable Termination Kit Included |  |  |  |
|  | Warranty |  |  |  |

- SURFACE PUMP REQUIREMENTS

D1. Pump Construction

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | VFD Compatible |  |  |  |
|  | Pump Efficiency≥60% |  |  |  |
|  | Impeller Material SS304 or better |  |  |  |
|  | Diffuser Material SS304 or better |  |  |  |
|  | Shaft Material Stainless Steel |  |  |  |
|  | Casing Material SS304/Duplex SS/Equivalent |  |  |  |
|  | Fasteners Stainless Steel |  |  |  |
|  | Bearings Tungsten Carbide or Equivalent |  |  |  |
|  | Mechanical Seal Silicon Carbide/Carbon |  |  |  |
|  | Operating Speed1850-2950 RPM |  |  |  |
|  | Performance Schedule Coverage Table 2.1B |  |  |  |
|  | Warranty24 Months Commissioning / 30 Months Delivery |  |  |  |

D2. SURFACE MOTOR REQUIREMENTS

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Type Three Phase AC |  |  |  |
|  | Voltage380-400 VAC |  |  |  |
|  | Frequency50 Hz |  |  |  |
|  | Rewindable |  |  |  |
|  | VFD Compatible |  |  |  |
|  | Insulation Class F Minimum |  |  |  |
|  | Tropicalized Winding |  |  |  |
|  | IP Rating IP55 Minimum |  |  |  |
|  | Efficiency ≤7.5kW≥80% |  |  |  |
|  | Efficiency >7.5kW ≥85% |  |  |  |
|  | Operating Speed 1850-2950 RPM |  |  |  |
|  | Warranty 24 Months Commissioning / 30 Months Delivery |  |  |  |

- MANDATORY DOCUMENT SUBMISSION CHECKLIST

| No. | Document Required | Submitted (Y/N) | Reference | Remark |
| --- | --- | --- | --- | --- |
| 1 | Pump Performance Curves |  |  |  |
| 2 | Hydraulic Datasheets |  |  |  |
| 3 | Motor Datasheets |  |  |  |
| 4 | Efficiency Curves |  |  |  |
| 5 | Power Consumption Curves |  |  |  |
| 6 | NPSHr Curves (Surface Pumps) |  |  |  |
| 7 | Pump Selection Reports |  |  |  |
| 8 | Factory Test Certificates |  |  |  |
| 9 | Guaranteed Duty Point Declaration |  |  |  |
| 10 | Warranty Certificate |  |  |  |
| 11 | Manufacturer Catalogue |  |  |  |
| 12 | Country of Origin Certificate |  |  |  |

- SOLAR PV SYSTEN AND DC ELECTRICAL WORK

- SOLAR PV MODULES

B1. General Information

| Item | Offered Details |
| --- | --- |
| Module type | Monocrystalline OR Bifacial N-Type TOPCon Module |
| Manufacturer |  |
| Model |  |
| Module Power (Wp) |  |
| Module Efficiency (%) |  |
| Country of Origin |  |

B2. Common Requirements (Applicable to Both Technologies)

| No. | Requirement | Minimum Requirement | Offered | Comply |
| --- | --- | --- | --- | --- |
| 1 | Module technology | Monocrystalline/ Bifacial |  |  |
| 2 | Manufacturer | Tier-1 Manufacturer |  |  |
| 3 | Rated power (Pmax) | ≥ 650 Wp |  |  |
| 4 | Module efficiency | ≥ 22% |  |  |
| 5 | Power tolerance | 0 to +5 W or better |  |  |
| 6 | Maximum system voltage | 1500 VDC |  |  |
| 7 | Cell type | Half-cut cells |  |  |
| 8 | Front glass | Tempered anti-reflective glass |  |  |
| 9 | Frame | Anodized aluminum alloy |  |  |
| 10 | Junction box protection | IP68 minimum |  |  |
| 11 | Connector type | MC4 compatible |  |  |
| 12 | Operating temperature | -40°C to +85°C or better |  |  |
| 13 | Wind load resistance | ≥ 2400 Pa |  |  |
| 14 | Snow load resistance | ≥ 5400 Pa |  |  |
| 15 | IEC certification | IEC 61215 |  |  |
| 16 | Safety certification | IEC 61730 |  |  |
| 17 | Quality certification | ISO 9001 |  |  |
| 18 | Environmental certification | ISO 14001 |  |  |
| 19 | safety certification | ISO 45001 |  |  |
| 20 | Product warranty | ≥ 12 years |  |  |
| 21 | Serial number identification | Required |  |  |
| 22 | Manufacturer datasheet | Required |  |  |
| 23 | Factory test report | Required |  |  |
| 24 | Warranty certificate | Required |  |  |

B3. Additional Requirements for Monocrystalline Modules (Option A)

| No. | Requirement | Minimum Requirement | Offered | Comply |
| --- | --- | --- | --- | --- |
| 1 | Module construction | Glass-back-sheet or equivalent |  |  |
| 2 | Module technology | N-Type TOPCon |  |  |
| 3 | Performance warranty | ≥ 25 years |  |  |
| 4 | Annual degradation rate | Manufacturer's declaration |  |  |
| 5 | Resistance to PID/LID | Required |  |  |

B3. Additional Requirements for Bifacial Modules (Option B)

| No. | Requirement | Minimum Requirement | Offered | Comply |
| --- | --- | --- | --- | --- |
| 1 | Module construction | Glass-Glass |  |  |
| 2 | Module technology | Bifacial N-Type TOPCon |  |  |
| 3 | BI faciality factor | ≥ 80% |  |  |
| 4 | Rear-side energy generation | Required |  |  |
| 5 | Performance warranty | ≥ 30 years preferred |  |  |
| 6 | Annual degradation rate | Manufacturer's declaration |  |  |
| 7 | Resistance to PID/LID/LeTID | Required |  |  |

- PV COMBINER BOX

- Compliance Schedule

| Item | Requirement | Compliance (Yes/No) | Offered Specification |
| --- | --- | --- | --- |
| Manufacturer | State Manufacturer |  |  |
| Model Number | State Model |  |  |
| Enclosure Material | Powder-Coated Stainless Steel / GRP |  |  |
| Protection | IP65 Minimum |  |  |
| Installation | Outdoor Rated |  |  |
| Max. DC Voltage | 1000/1500 VDC |  |  |
| No. of String Inputs | No. string + 2 Spare |  |  |
| String Fuse Type | PV Rated gPV |  |  |
| String Fuse Rating | ≥ 1.25 × Isc |  |  |
| Main DC Isolator | Included |  |  |
| DC Isolator Voltage | 1000/1500 VDC |  |  |
| DC Isolator Rating | ≥ 125% of Array Current |  |  |
| DC Circuit Breaker | Included/integrated |  |  |
| Surge Protection | SPD Type I or Type II |  |  |
| SPD Indicator | Required |  |  |
| Replaceable SPD Modules | Required |  |  |
| Reverse Current Protection | Required |  |  |
| Busbar Material | Tinned Copper |  |  |
| Busbar Capacity | ≥ 125% of String Current |  |  |
| String Terminations | MC4 Compatible |  |  |
| Cable Glands | IP68 UV-Resistant |  |  |
| DIN Rail Mounting | Required |  |  |
| Earthing Bar | Required |  |  |
| Equipotential Bonding | Required |  |  |
| Safety Labels | Required |  |  |
| String Identification Labels | Required |  |  |
| DC Warning Labels | Required |  |  |
| Operating Temperature | -30°C to +70°C Minimum |  |  |
| Factory Assembly | Required |  |  |
| Factory Testing | Required |  |  |
| Warranty | Minimum 2 Years |  |  |

- SOLAR PUMP INVERTER / CONTROLLER

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Hybrid Solar Pump Inverter |  |  |  |
|  | Integrated MPPT |  |  |  |
|  | Integrated VFD |  |  |  |
|  | Data Logging |  |  |  |
|  | Hybrid Power Management |  |  |  |
|  | Capacity1.5-350kW |  |  |  |
|  | Inverter Sizing≥1.25 × Pump kW |  |  |  |
|  | Output Voltage380/415VAC |  |  |  |
|  | Three Phase Output |  |  |  |
|  | Frequency50Hz |  |  |  |
|  | Efficiency≥95% |  |  |  |
|  | Protection Rating IP55 Minimum |  |  |  |
|  | DC Input Voltage1000VDC |  |  |  |
|  | Operating Temperature Up to +45°C |  |  |  |
|  | Soft Start Function |  |  |  |
|  | Automatic MPPT Tracking |  |  |  |
|  | Automatic Start/Stop |  |  |  |
|  | Generator Integration |  |  |  |
|  | Grid Integration |  |  |  |
|  | Water Level Monitoring |  |  |  |
|  | Dry Run Protection |  |  |  |
|  | Tank Full Protection |  |  |  |
|  | High Pressure Protection |  |  |  |
|  | Fault Diagnostics |  |  |  |
|  | LCD Display |  |  |  |
|  | Remote Monitoring |  |  |  |
|  | Warranty |  |  |  |

- EARTHING & BONDING SYSTEM

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Soil Resistivity Test Wenner Method |  |  |  |
|  | Earth Rod Type pure Copper Bonded Steel |  |  |  |
|  | Earth Rod Diameter ≥16 mm |  |  |  |
|  | Earth Rod Length ≥1.5 m |  |  |  |
|  | Copper Coating ≥250 Micron |  |  |  |
|  | Earth Connections Exothermic Welded |  |  |  |
|  | Ring Earth System |  |  |  |
|  | Earth Grid Conductor |  |  |  |
|  | Earth Enhancement Material |  |  |  |
|  | Equipment Bonding |  |  |  |
|  | Earth Resistance |  |  |  |
|  | Continuity Testing |  |  |  |
|  | As-Built Drawings |  |  |  |

- LIGHTNING PROTECTION SYSTEM

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | IEC 62305 Compliance |  |  |  |
|  | Lightning Risk Assessment |  |  |  |
|  | ESE Air Terminal |  |  |  |
|  | Mast Height Minimum 6m |  |  |  |
|  | Down Conductors Copper |  |  |  |
|  | Exothermic Welds |  |  |  |
|  | Type 1 SPD |  |  |  |
|  | Type 2 SPD |  |  |  |
|  | Dedicated Lightning Earth |  |  |  |
|  | Earth Resistance≤1 Ohm Where |  |  |  |
|  | Continuity Testing |  |  |  |

- SOLAR LED SECURITY LIGHTS

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | All-in-One Design |  |  |  |
|  | LED Efficacy≥150 lm/W |  |  |  |
|  | Luminous Flux1500-3000 Lumens |  |  |  |
|  | Solar Module Monocrystalline ≥20% |  |  |  |
|  | Battery Type LiFePO4 |  |  |  |
|  | Autonomy Minimum 2-3 Nights |  |  |  |
|  | MPPT Controller |  |  |  |
|  | PIR Sensor Integrated |  |  |  |
|  | Pole Height4-6 m |  |  |  |
|  | IP Protection IP65 Minimum |  |  |  |
|  | Impact Protection IK08 Minimum |  |  |  |
|  | Wind Resistance≥150 km/hr |  |  |  |
|  | Warranty Minimum 5 Years |  |  |  |

- PV CLEANING EQUIPMENT

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Wet Cleaning Mode |  |  |  |
|  | Dry Cleaning Mode |  |  |  |
|  | Brush Width ≥600 mm |  |  |  |
|  | Water Purification RO/Ion Exchange |  |  |  |
|  | Water Conductivity<10 μS/cm |  |  |  |
|  | Battery Powered |  |  |  |
|  | Operating Time ≥8 Hours |  |  |  |
|  | Emergency Stop |  |  |  |
|  | Overload Protection |  |  |  |
|  | Reach 4-6 m |  |  |  |
|  | Spare Brushes Included |  |  |  |
|  | Spare Filters Included |  |  |  |
|  | Warranty Minimum 2 Years |  |  |  |

- FIRE EXTINGUISHERS

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Quantity 2 per Facility |  |  |  |
|  | Type (ABC) Dry Powder |  |  |  |
|  | Standard EN1866 |  |  |  |
|  | Capacity 4, 5, 6, 9, 12 kg |  |  |  |
|  | Mounting Near Inverter Area |  |  |  |
|  | Signage Photoluminescent Signs |  |  |  |
|  | Inspection Certificates |  |  |  |
|  | Pressure Test Certificates |  |  |  |
|  | Warranty Minimum 2 Years |  |  |  |

- DOCUMENTATION SUBMISSION CHECKLIST

| No. | Required Document | Submitted | Reference |
| --- | --- | --- | --- |
|  | PV Module Datasheets |  |  |
|  | Module Certifications |  |  |
|  | I-V Curves |  |  |
|  | P-V Curves |  |  |
|  | Combiner Box Datasheet |  |  |
|  | Inverter Datasheet |  |  |
|  | Cable Datasheets |  |  |
|  | Earthing Design Report |  |  |
|  | Lightning Protection Design |  |  |
|  | Factory Test Certificates |  |  |
|  | Warranty Certificates |  |  |
|  | As-Built Drawings |  |  |
|  | O&M Manuals |  |  |
|  | Training Records |  |  |
|  | Commissioning Reports |  |  |

- BACKUP POWER SUPPLY WORK

- GENESET COMPLIANCE SCHEDULE

| Parameter | Requirement | Comply (Yes/No) | Offered Specification |
| --- | --- | --- | --- |
| Diesel Engine Generator Set | Required |  |  |
| Capacity ≥ 120% Connected Load | Required |  |  |
| 400/220 VAC, 50 Hz, 3-Phase | Required |  |  |
| Voltage Regulation ±1% | Required |  |  |
| Frequency Regulation ±1% | Required |  |  |
| THD ≤ 5% | Required |  |  |
| 24 VDC Electric Starting | Required |  |  |
| Water-Cooled Engine | Required |  |  |
| Brushless Alternator | Required |  |  |
| AVR Equipped | Required |  |  |
| Insulation Class H | Required |  |  |
| IP23 Minimum Alternator Protection | Required |  |  |
| Auto Start/Stop Controller | Required |  |  |
| Remote Start Capability | Required |  |  |
| Event Logging | Required |  |  |
| Complete Protection Functions | Required |  |  |
| 24-Hour Fuel Storage Capacity | Required |  |  |
| Fuel Gauge and Drain Valve | Required |  |  |
| Weatherproof Acoustic Enclosure | Required |  |  |
| Noise Level ≤ 75 dBA @ 1 m | Required |  |  |
| RCC Foundation Included | Required |  |  |
| Anti-Vibration Mounts Included | Required |  |  |
| FAT Conducted | Required |  |  |
| Load Bank Testing Conducted | Required |  |  |
| Training Included | Required |  |  |
| O&M Manuals Submitted | Required |  |  |
| Warranty Documentation Submitted | Required |  |  |

Manufacturer Information

| Item | Offered |
| --- | --- |
| Generator Manufacturer |  |
| Generator Model |  |
| Engine Manufacturer |  |
| Engine Model |  |
| Alternator Manufacturer |  |
| Alternator Model |  |
| Standby Rating (kVA) |  |
| Prime Rating (kVA) |  |
| Fuel Tank Capacity (L) |  |
| Noise Level (dBA) |  |
| Warranty Period |  |

- AUTOMATIC TRANSFER SWITCH (ATS)

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Standard IEC 60947-6-1 |  |  |  |
|  | Configuration4 Pole (3P+N) |  |  |  |
|  | Voltage 400/230V |  |  |  |
|  | Frequency 50 Hz |  |  |  |
|  | Current Rating ≥125% Load Current |  |  |  |
|  | Fully Switched Neutral |  |  |  |
|  | Mechanical Interlock |  |  |  |
|  | Electrical Operation |  |  |  |
|  | Manual Emergency Operation |  |  |  |
|  | Generator Auto Start Signal |  |  |  |
|  | Generator Auto Stop Signal |  |  |  |
|  | Automatic Re-transfer |  |  |  |
|  | Adjustable Time Delays |  |  |  |
|  | Phase Failure Protection |  |  |  |
|  | Phase Sequence Monitoring |  |  |  |
|  | Under Voltage Protection |  |  |  |
|  | Over Voltage Protection |  |  |  |
|  | Under Frequency Protection |  |  |  |
|  | Over Frequency Protection |  |  |  |
|  | LCD Display Digital LCD/HMI |  |  |  |
|  | Event Logging |  |  |  |
|  | Alarm Indication |  |  |  |
|  | Test Mode |  |  |  |
|  | RS485/Modbus Communication |  |  |  |
|  | Remote Monitoring |  |  |  |
|  | Enclosure Rating Indoor IP54 Minimum |  |  |  |
|  | Enclosure Rating Outdoor IP65 Minimum |  |  |  |
|  | Factory Test Certificate |  |  |  |
|  | Warranty24 Months Minimum |  |  |  |

- MANUAL CHANGEOVER SWITCH (COS)

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Standard IEC 60947-3 |  |  |  |
|  | Pole Arrangement 4 Pole |  |  |  |
|  | Operating Voltage 400/230V |  |  |  |
|  | Frequency50Hz |  |  |  |
|  | Current Rating ≥125% Load Current |  |  |  |
|  | Switching Positions Grid-Off-Generator |  |  |  |
|  | Break Before Make |  |  |  |
|  | Mechanical Interlock |  |  |  |
|  | Switched Neutral |  |  |  |
|  | Lockable Handle |  |  |  |
|  | Padlocking Facility |  |  |  |
|  | Enclosure IP Rating |  |  |  |
|  | Permanent Labels |  |  |  |
|  | Warranty Minimum 24 Months |  |  |  |

- BATTERY ENERGY STORAGE SYSTEM (BESS)

D1. General Information

| Item | Offered Details |
| --- | --- |
| Manufacturer |  |
| Model |  |
| Battery Chemistry |  |
| Capacity (kWh) |  |
| Autonomy (hrs) |  |

D2. Technical Requirements

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Battery Chemistry LiFePO4 Only |  |  |  |
|  | Standard Compliance IEC 62619 / UL1973 |  |  |  |
|  | Autonomy Minimum 6 Hours |  |  |  |
|  | Cycle Life ≥6000 Cycles |  |  |  |
|  | Round Trip Efficiency≥95% |  |  |  |
|  | IP Rating IP55 Minimum |  |  |  |
|  | Operating Temperature-20°C to +55°C |  |  |  |
|  | Communication CAN / RS485 |  |  |  |
|  | Capacity Retention ≥70% after 10 Years |  |  |  |

D3. Safety Features

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Integrated BMS |  |  |  |
|  | Cell Balancing |  |  |  |
|  | Short Circuit Protection |  |  |  |
|  | Ground Fault Monitoring |  |  |  |
|  | Overcharge Protection |  |  |  |
|  | Over-discharge Protection |  |  |  |
|  | Over-temperature Protection |  |  |  |
|  | Fire Alarm Interface |  |  |  |
|  | Emergency Isolation Switch |  |  |  |

D4. HYBRID INVERTER SYSTEM

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Grid Operation |  |  |  |
|  | Battery Operation |  |  |  |
|  | Generator Operation |  |  |  |
|  | Hybrid Operation |  |  |  |
|  | Automatic Source Selection |  |  |  |
|  | Efficiency≥98% |  |  |  |
|  | MPPT Efficiency≥99% |  |  |  |
|  | Automatic Synchronization |  |  |  |
|  | THD≤3% |  |  |  |
|  | Power Factor Range0.9 Lagging to 0.9 Leading |  |  |  |
|  | Reverse Polarity Protection |  |  |  |
|  | Short Circuit Protection |  |  |  |
|  | Ground Fault Protection |  |  |  |
|  | Surge Protection |  |  |  |
|  | Anti-Islanding |  |  |  |
|  | Web Monitoring |  |  |  |
|  | GSM/4G Monitoring |  |  |  |
|  | RS485 Communication |  |  |  |
|  | Historical Data Logging |  |  |  |
|  | Alarm Notification |  |  |  |
|  | Warranty60 Months |  |  |  |

- GRID INTERCONNECTION SYSTEM

E1. Low Voltage Grid Connection

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | LV Connection Voltage400/230VAC |  |  |  |
|  | LV Interconnection Panel Complete Assembly |  |  |  |
|  | MCCB Incomer |  |  |  |
|  | MCCB Outgoings |  |  |  |
|  | Revenue Meter Utility Approved |  |  |  |
|  | Type 1/2 SPD |  |  |  |
|  | Earthing & Bonding |  |  |  |
|  | Protection Devices |  |  |  |
|  | Lockable Enclosure IP54/IP65 |  |  |  |

E2. Transformer/MV Connection

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Transformer IEC 60076 Compliant |  |  |  |
|  | Voltage Ratio15/0.4kV or 33/0.4kV |  |  |  |
|  | Vector Group Dyn11 |  |  |  |
|  | RMU/LBS |  |  |  |
|  | Surge Arresters |  |  |  |
|  | Utility Metering |  |  |  |
|  | Numerical Protection Relays |  |  |  |
|  | Earthing System |  |  |  |
|  | Utility Approval |  |  |  |

E3. TESTING, TRAINING & DOCUMENTATION

Testing & Commissioning

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Generator FAT |  |  |  |
|  | ATS FAT |  |  |  |
|  | Battery FAT |  |  |  |
|  | Inverter FAT |  |  |  |
|  | Generator Load Test |  |  |  |
|  | ATS Functional Test |  |  |  |
|  | Battery Discharge Test |  |  |  |
|  | Insulation Resistance Test |  |  |  |
|  | Earth Resistance Test |  |  |  |
|  | Synchronization Test |  |  |  |

E4`Training Requirements

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Minimum Training Duration2 Days |  |  |  |
|  | Generator Operation Training |  |  |  |
|  | ATS Operation Training |  |  |  |
|  | Battery Management Training |  |  |  |
|  | Hybrid Inverter Training |  |  |  |
|  | Maintenance Training |  |  |  |
|  | Safety Procedures Training |  |  |  |
|  | Troubleshooting Training |  |  |  |

E5. Required Documentation

| No. | Document | Submitted | Reference |
| --- | --- | --- | --- |
|  | Load Calculations |  |  |
|  | Generator Sizing Calculations |  |  |
|  | Battery Sizing Calculations |  |  |
|  | Single Line Diagram |  |  |
|  | Equipment Datasheets |  |  |
|  | Shop Drawings |  |  |
|  | Protection Settings Report |  |  |
|  | FAT Certificates |  |  |
|  | SAT Reports |  |  |
|  | O&M Manuals |  |  |
|  | Warranty Certificates |  |  |
|  | As-Built Drawings |  |  |

E6. WARRANTY COMPLIANCE

| Equipment | Offered | Compliance | Evidence |
| --- | --- | --- | --- |
| Generator Set24 Months / 2000 Hours |  |  |  |
| ATS24 Months |  |  |  |
| Switchgear24 Months |  |  |  |
| Hybrid Inverter60 Months |  |  |  |
| Battery Product Warranty60 Months |  |  |  |
| Battery Performance Warranty10 Years |  |  |  |
| Monitoring Equipment24 Months |  |  |  |

- BOREHOLE RISERS, CASINGS, PIPES & FITTINGS

- GENERAL REQUIREMENTS

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Scope of Supply, Delivery, Installation, Testing & Commissioning |  |  |  |
|  | Potable Water Approval |  |  |  |
|  | International Standards Compliance ISO/ASTM/EN/AWWA/BS |  |  |  |
|  | Pressure Testing |  |  |  |
|  | Flushing & Disinfection |  |  |  |
|  | As-Built Drawings |  |  |  |
|  | Warranty Support |  |  |  |

- BOREHOLE RISER PIPES & ACCESSORIES

B1. Riser Pipe

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Pipe Type GI / SS304 / SS316 / uPVC PN16 |  |  |  |
|  | Pressure Rating PN10-PN30 as Applicable |  |  |  |
|  | Pipe Length6m Standard (3m acceptable) |  |  |  |
|  | Potable Water Suitable |  |  |  |
|  | Joint Type Threaded / Flanged / ZSM |  |  |  |
|  | Complete Adaptors Included |  |  |  |

2. GI Carbon Steel Riser Pipes

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Material Hot Dip Galvanized Carbon Steel |  |  |  |
|  | Standard BS1387 or Equivalent |  |  |  |
|  | Joint Type Threaded/Flanged |  |  |  |
|  | Heavy Duty Schedule |  |  |  |

B3. Stainless Steel Riser Pipes

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Material Grade AISI 304 / 316 |  |  |  |
|  | Pipe Type Seamless/Welded |  |  |  |
|  | Diameter Range DN50-DN100 |  |  |  |
|  | Pressure Rating PN10-PN16 Minimum |  |  |  |
|  | ZSM Couplings Available |  |  |  |
|  | EPDM Seals |  |  |  |

B4. Downhole Support Accessories

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Cable Clamps Heavy Duty PP |  |  |  |
|  | Guide Brackets |  |  |  |
|  | Cable Fixing Interval Every 3m |  |  |  |
|  | Quantity1 Clamp Per 3m Pipe |  |  |  |

- WELLHEAD OUTLET MANIFOLD & APPURTENANCES

C1. Manifold Fabrication

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Pipe Material HDG Steel / SS304 / SS316 |  |  |  |
|  | Pressure Class PN16 Minimum |  |  |  |
|  | Diameter Range DN50-DN150 |  |  |  |
|  | Flanged Connections |  |  |  |
|  | Hot Dip Galvanizing≥85 Microns |  |  |  |
|  | Shop Fabrication |  |  |  |

C2. Mandatory Manifold Components

| Ref. | Component | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Riser Head Connection HDG/SS Flanged Assembly |  |  |  |
|  | Vertical Riser Extension PN16 Minimum |  |  |  |
|  | Dismantling Joint Adjustable Flanged Type |  |  |  |
|  | Gate Valve BS5163, PN16 |  |  |  |
|  | Non Return Valve Swing Check Type PN16 |  |  |  |
|  | Electromagnetic Flow Meter IP68, ±0.5% Accuracy |  |  |  |
|  | Air Valve Assembly Double Orifice DN50 PN16 |  |  |  |
|  | Pressure Gauge SS Housing, 100mm Dial |  |  |  |
|  | Pressure Switch IP65, NO/NC Contacts |  |  |  |
|  | Sampling Assembly SS304 Minimum |  |  |  |
|  | Pressure Relief Valve Pilot Operated PN16 |  |  |  |
|  | Surge Vessel Bladder Type, 2m³ Minimum |  |  |  |
|  | Pipe Supports HDG Supports & Anchors |  |  |  |

C3. Testing & Warranty

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Hydrostatic Test Pressure1.5 x Working Pressure |  |  |  |
|  | Test Duration2 Hours Minimum |  |  |  |
|  | No Leakage |  |  |  |
|  | Calibration Certificates |  |  |  |
|  | Warranty Minimum 24 Months |  |  |  |

- WELLHEAD COVER ASSEMBLY

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Material HDG Steel or SS316 |  |  |  |
|  | Cover Thickness Minimum 18mm |  |  |  |
|  | Corrosion Protection HDG 85μm or SS316 |  |  |  |
|  | Watertight Design |  |  |  |
|  | Locking System Stainless Steel Lockable |  |  |  |
|  | EPDM Gasket Minimum 5mm |  |  |  |
|  | Vent Assembly SS Vent with Rain Hood |  |  |  |
|  | Cable Entry Glands IP68 |  |  |  |
|  | Lifting Handles Minimum Two |  |  |  |
|  | Identification Plate Stainless Steel Engraved |  |  |  |
|  | Water Tightness Test |  |  |  |
|  | Material Certificates |  |  |  |

- BOREHOLE CASING & SCREENS

E1. General Requirements

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | New Pipe Material |  |  |  |
|  | Straight & Defect Free |  |  |  |
|  | International Standard ISO/ASTM/DIN Compliant |  |  |  |
|  | Watertight Joints |  |  |  |
|  | Collapse Resistance |  |  |  |
|  | Hydrostatic Test Certificate |  |  |  |
|  | Manufacturer Marking |  |  |  |

E2. uPVC Casing Pipes

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Material uPVC Potable Water Grade |  |  |  |
|  | Standard ASTM D1785 / DIN4925 / ISO4422 |  |  |  |
|  | Service Life50 Years Minimum |  |  |  |
|  | Pressure Rating PN10 Minimum |  |  |  |
|  | Wall Thickness≥6mm to 12mm |  |  |  |

E3. Steel Casing Pipes

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Material High Strength Carbon Steel |  |  |  |
|  | Standard API 5L / ASTM A53 |  |  |  |
|  | Anti-Corrosion Coating |  |  |  |
|  | Yield Strength≥240MPa |  |  |  |
|  | Wall Thickness≥6-12mm |  |  |  |

E4. Borehole Screens

| Ref. No. | Requirement | Required Specification | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Screen Material | Same as Casing |  |  |
|  | Slot Size | 0.5 - 1.0 mm |  |  |
|  | Open Area | ≥10% |  |  |
|  | Screen Length | As Design |  |  |

- PIPES & FITTINGS

F1. Pipe Materials

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Minimum Pressure Rating PN16 |  |  |  |
|  | Potable Water Certification WRAS/NSF Equivalent |  |  |  |
|  | Hydraulic Velocity Range0.5 to 2.5 m/s |  |  |  |

F2. HDPE Pipes

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Standard ISO 4427 |  |  |  |
|  | Material PE100 |  |  |  |
|  | Jointing Butt Fusion/Electrofusion |  |  |  |
|  | Pressure Rating PN16 |  |  |  |

F3. Ductile Iron Pipes

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Standard EN545 / AWWA C151 |  |  |  |
|  | Cement Mortar Lining |  |  |  |
|  | External Coating PE Sleeve/Bituminous |  |  |  |
|  | Joint Type TYTON/Flanged |  |  |  |

F4. uPVC Pipes

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Standard AWWA C900 |  |  |  |
|  | Class Rating Class 150/200 |  |  |  |
|  | Joint Type Solvent/Rubber Ring |  |  |  |

F5. GRP Pipes

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Standard ISO14692 / AWWA C950 |  |  |  |
|  | Joint Type O-Ring/Flanged |  |  |  |

- VALVES & FITTINGS

| No. | Requirement | Offered | Compliance | Evidence |
| --- | --- | --- | --- | --- |
|  | Gate Valve AWWA C509 / EN1074 |  |  |  |
|  | Butterfly Valve AWWA C504 / EN593 |  |  |  |
|  | Check Valve AWWA C508 |  |  |  |
|  | Air Valve EN1074-4 |  |  |  |
|  | Drain Valve Resilient Seated Type |  |  |  |
|  | Fire Hydrant AWWA C502 / BS750 |  |  |  |
|  | Elbows22.5°, 45°, 90° |  |  |  |
|  | Tees Equal & Reducing |  |  |  |
|  | Reducers |  |  |  |
|  | Flanged Adaptors |  |  |  |
|  | Dismantling Joints |  |  |  |

BIDDER TECHNICAL COMPLIANCE DECLARATION FORM

Tender Reference No.: ___________________________

Tender Title: ___________________________________

Bidder Information

Company Name: ___________________________________

Address: _________________________________________

Contact Person: _________________________________

Telephone: ______________________________________

Email: __________________________________________

Technical Compliance Declaration

I/We, the undersigned, hereby declare that:

- We have carefully reviewed the technical specifications, requirements, scope of work, and conditions outlined in the bidding document.

- We confirm that the goods, services, or works offered under this bid comply with all technical requirements and specifications stated in the tender document, except for any deviations specifically disclosed in our technical proposal.

- We acknowledge that supporting technical documents, brochures, catalogs, drawings, certificates, and other evidence submitted with our bid accurately represent the offered goods, services, or works.

- We undertake to deliver, install, commission, and/or perform the required goods, services, or works in accordance with the technical requirements and timelines specified in the bidding documents.

- We understand that any false technical information or misrepresentation may result in the rejection of our bid, termination of any resulting contract, and/or other remedies available to the procuring entity.

- We certify that all products, materials, equipment, and services proposed are fit for their intended purpose and conform to the applicable standards, specifications, and regulatory requirements.

Authorized Representative

Name: _______________________________________

Position/Title: ________________________________

Company Name: ________________________________

Signature: _____________________________________

Date: _________________________________________

Company Stamp/Seal: ___________________________

Declaration: I certify that the information provided in this Technical Compliance Declaration is true and correct, and that I am duly authorized to sign this declaration on behalf of the bidder.

# Attachement-2: Schedules: pump performance, solar PV Modules and Fencing

Note to Bidders

The performance envelope represents the minimum required hydraulic operating range. Bidders may demonstrate compliance using a single pump performance curve or, where necessary, up to three pump performance curves.

Where more than one curve is submitted, all curves shall belong to the same pump family and manufacturer and shall be derived from the manufacturer's published performance data. The curves may represent different impeller diameters, stage numbers, or other standard hydraulic configurations within the same pump family.

The submitted curve(s) shall collectively demonstrate compliance with the specified performance envelope and guaranteed duty points.

A separate Guaranteed Performance Schedule and Price Schedule shall be submitted for each curve.

For each curve submitted, the bidder shall provide:

- Pump performance curve (Head vs. Flow);

- Efficiency curve;

- Absorbed power curve;

- Technical datasheet;

- Motor rating;

- Guaranteed duty point data.

The guaranteed hydraulic efficiency at the Low Head, Medium Head, and High Head Duty Points shall not be less than 60%.

The motor power indicated in the Performance Schedule represents the Maximum Motor Power Rating for the specified performance envelope. Pumps with lower motor power ratings may be offered, provided that all specified performance and efficiency requirements are satisfied.

Suggested separate Price Schedule if multiple curve per pump size

| Item No. | Curve No. | Pump Family/Model | Motor Power (kW) | Unit | Qty | Unit Price |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Curve 1 | Bidder to State | Bidder to State | No. | 1 |  |
|  | Curve 2 | Bidder to State | Bidder to State | No. | 1 |  |
|  | Curve 3 | Bidder to State | Bidder to State | No. | 1 |  |

Table 2.1A: SUBMERSIBLE PUMP MINIMUM PERFORMANCE ENVELOPE AND GAURANTED DUTY POINTS, Efficiency ≥65%

| Model No. | Motor Pump (KW) | Flow Range Q(m3/h) | Head Range H(m3/h) | Low head Duty point (Q @ TDH) | Medium head Duty point (Q @ TDH) | High head Duty point (Q @ TDH) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 0.75 | 1-4 | 40-160 | 4 m³/h @ 40 m | 2.5 m³/h @ 64.8 m | 1 m³/h @ 160 m |
| 2 | 1.5 | 3-5 | 65-100 | 5 m³/h @ 65 m | 4 m³/h @ 81.0 m | 3 m³/h @ 100 m |
| 3 | 2.2 | 3-6 | 80-170 | 6 m³/h @ 80 m | 4.5 m³/h @ 105.6 m | 3 m³/h @ 170 m |
| 4 | 3.7 | 3-9 | 90-270 | 9 m³/h @ 90 m | 6 m³/h @ 133.2 m | 3 m³/h @ 270 m |
| 5 | 5.5 | 4-12 | 100-300 | 12 m³/h @ 100 m | 8 m³/h @ 148.5 m | 4 m³/h @ 300 m |
| 6 | 7.5 | 5-20 | 80-325 | 20 m³/h @ 80 m | 12.5 m³/h @ 129.6 m | 5 m³/h @ 325 m |
| 7 | 9.3 | 10-25 | 80-200 | 25 m³/h @ 80 m | 17.5 m³/h @ 114.8 m | 10 m³/h @ 200 m |
| 8 | 11 | 8-20 | 120-300 | 20 m³/h @ 120 m | 14 m³/h @ 169.7 m | 8 m³/h @ 300 m |
| 9 | 15 | 12-24 | 135-270 | 24 m³/h @ 135 m | 18 m³/h @ 180.0 m | 12 m³/h @ 270 m |
| 10 | 18.5 | 12-40 | 100-350 | 40 m³/h @ 100 m | 26 m³/h @ 153.7 m | 12 m³/h @ 350 m |
| 11 | 22 | 16-40 | 120-300 | 40 m³/h @ 120 m | 28 m³/h @ 169.7 m | 16 m³/h @ 300 m |
| 12 | 26 | 20-50 | 110-280 | 50 m³/h @ 110 m | 35 m³/h @ 160.5 m | 20 m³/h @ 280 m |
| 13 | 30 | 20-50 | 130-325 | 50 m³/h @ 130 m | 35 m³/h @ 185.1 m | 20 m³/h @ 325 m |
| 14 | 37 | 20-50 | 160-400 | 50 m³/h @ 160 m | 35 m³/h @ 228.3 m | 20 m³/h @ 400 m |
| 15 | 45 | 30-70 | 140-325 | 70 m³/h @ 140 m | 50 m³/h @ 194.4 m | 30 m³/h @ 325 m |
| 16 | 55 | 40-100 | 120-300 | 100 m³/h @ 120 m | 70 m³/h @ 169.7 m | 40 m³/h @ 300 m |
| 17 | 63 | 45-100 | 140-300 | 100 m³/h @ 140 m | 72.5 m³/h @ 187.7 m | 45 m³/h @ 300 m |
| 18 | 75 | 45-100 | 160-360 | 100 m³/h @ 160 m | 72.5 m³/h @ 223.4 m | 45 m³/h @ 360 m |
| 19 | 90 | 50-120 | 160-390 | 120 m³/h @ 160 m | 85 m³/h @ 228.7 m | 50 m³/h @ 390 m |
| 20 | 110 | 80-200 | 120-300 | 200 m³/h @ 120 m | 140 m³/h @ 169.7 m | 80 m³/h @ 300 m |
| 21 | 132 | 90-200 | 145-320 | 200 m³/h @ 145 m | 145 m³/h @ 196.6 m | 90 m³/h @ 320 m |
| 22 | 160 | 100-200 | 175-345 | 200 m³/h @ 175 m | 150 m³/h @ 230.4 m | 100 m³/h @ 345 m |
| 23 | 185 | 120-250 | 160-330 | 250 m³/h @ 160 m | 185 m³/h @ 216.0 m | 120 m³/h @ 330 m |
| 24 | 200 | 120-250 | 175-360 | 250 m³/h @ 175 m | 185 m³/h @ 233.5 m | 120 m³/h @ 360 m |
| 25 | 250 | 140-250 | 210-385 | 250 m³/h @ 210 m | 195 m³/h @ 276.9 m | 140 m³/h @ 385 m |

Table 2.1B: SURFACE PUMP MINIMUM PERFORMANCE ENVELOPE AND GAURANTED DUTY POINTS, Efficiency ≥65%

| Model No. | Motor Pump (KW) | Flow Range Q(m3/h) | Head Range H(m3/h) | Low head Duty point (Q @ TDH) | Medium head Duty point (Q @ TDH) | High head Duty point (Q @ TDH) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 0.75 | 2-4 | 40-80 | 4 m³/h @ 40 m | 3 m³/h @ 54 m | 2 m³/h @ 80 m |
| 2 | 1.5 | 3-5 | 65-160 | 5 m³/h @ 65 m | 4 m³/h @ 81 m | 3 m³/h @ 160 m |
| 3 | 2.2 | 3-8 | 60-160 | 8 m³/h @ 60 m | 5.5 m³/h @ 86.4 m | 3 m³/h @ 160 m |
| 4 | 3.7 | 3-8 | 100-270 | 8 m³/h @ 100 m | 5.5 m³/h @ 145.3 m | 3 m³/h @ 270 m |
| 5 | 5.5 | 8-12 | 100-150 | 12 m³/h @ 100 m | 10 m³/h @ 118.8 m | 8 m³/h @ 150 m |
| 6 | 7.5 | 12-25 | 65-140 | 25 m³/h @ 65 m | 18.5 m³/h @ 87.6 m | 12 m³/h @ 140 m |
| 7 | 9.3 | 12-25 | 80-170 | 25 m³/h @ 80 m | 18.5 m³/h @ 108.6 m | 12 m³/h @ 170 m |
| 8 | 11 | 12-65 | 40-200 | 65 m³/h @ 40 m | 38.5 m³/h @ 61.7 m | 12 m³/h @ 200 m |
| 9 | 15 | 15-45 | 72-220 | 45 m³/h @ 72 m | 30 m³/h @ 108 m | 15 m³/h @ 220 m |
| 10 | 18.5 | 25-50 | 80-160 | 50 m³/h @ 80 m | 37.5 m³/h @ 106.6 m | 25 m³/h @ 160 m |
| 11 | 22 | 30-90 | 50-160 | 90 m³/h @ 50 m | 60 m³/h @ 79.2 m | 30 m³/h @ 160 m |
| 12 | 26 | 20-40 | 140-280 | 40 m³/h @ 140 m | 30 m³/h @ 187.2 m | 20 m³/h @ 280 m |
| 13 | 30 | 30-150 | 40-220 | 150 m³/h @ 40 m | 90 m³/h @ 72 m | 30 m³/h @ 220 m |
| 14 | 37 | 30-120 | 65-265 | 120 m³/h @ 65 m | 75 m³/h @ 106.6 m | 30 m³/h @ 265 m |
| 15 | 45 | 40-120 | 80-240 | 120 m³/h @ 80 m | 80 m³/h @ 121.5 m | 40 m³/h @ 240 m |
| 16 | 55 | 40-150 | 80-300 | 150 m³/h @ 80 m | 95 m³/h @ 125.1 m | 40 m³/h @ 300 m |
| 17 | 63 | 40-150 | 90-340 | 150 m³/h @ 90 m | 95 m³/h @ 143.2 m | 40 m³/h @ 340 m |
| 18 | 75 | 70-140 | 115-230 | 140 m³/h @ 115 m | 105 m³/h @ 154.3 m | 70 m³/h @ 230 m |
| 19 | 90 | 80-160 | 120-245 | 160 m³/h @ 120 m | 120 m³/h @ 162 m | 80 m³/h @ 245 m |
| 20 | 110 | 120-180 | 130-200 | 180 m³/h @ 130 m | 150 m³/h @ 158.4 m | 120 m³/h @ 200 m |
| 21 | 132 | 90-200 | 140-320 | 200 m³/h @ 140 m | 145 m³/h @ 196.6 m | 90 m³/h @ 320 m |
| 22 | 160 | 100-200 | 170-345 | 200 m³/h @ 170 m | 150 m³/h @ 230.4 m | 100 m³/h @ 345 m |
| 23 | 185 | 150-250 | 160-270 | 250 m³/h @ 160 m | 200 m³/h @ 199.8 m | 150 m³/h @ 270 m |
| 24 | 200 | 140-240 | 280-300 | 240 m³/h @ 280 m | 190 m³/h @ 227.4 m | 140 m³/h @ 300 m |
| 25 | 250 | 180-280 | 290-300 | 280 m³/h @ 290 m | 230 m³/h @ 234.8 m | 180 m³/h @ 300 m |

Table 2.1C: SCHEDULE FOR WELDED MESH FENCING FOR SOLAR PV COMPOUND

| Model ID | Motor Pump (KW) | Solar Array (kWp) | Perimeter Length (m) | Posts w/ lugs 3m (pcs) | C25 footing (m3) | Mesh panel (Pcs) | C25 Curbs (m3) | Type 1 Gate 1m (pcs) | Type 2 Gate 3m (pcs) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 0.75 | 1.5 | 32 | 14 | 0.6 | 13 | 1.9 | 1 | - |
| 2 | 1.5 | 3 | 42 | 18 | 0.8 | 17 | 2.5 | 1 | - |
| 3 | 2.2 | 4 | 44 | 19 | 0.8 | 18 | 2.6 | 1 | - |
| 4 | 3.7 | 7.2 | 44 | 19 | 0.8 | 18 | 2.6 | 1 | - |
| 5 | 5.5 | 10.4 | 44 | 19 | 0.8 | 18 | 2.6 | 1 | - |
| 6 | 7.5 | 14.4 | 62 | 26 | 1.1 | 25 | 3.7 | 1 | - |
| 7 | 9.3 | 17.6 | 56 | 23 | 1.0 | 22 | 3.4 | 1 | - |
| 8 | 11 | 21.6 | 56 | 23 | 1.0 | 22 | 3.4 | 1 | - |
| 9 | 15 | 26.4 | 70 | 29 | 1.2 | 28 | 4.2 | 1 | - |
| 10 | 18.5 | 35.2 | 74 | 31 | 1.3 | 30 | 4.4 | 1 | - |
| 11 | 22 | 41.6 | 74 | 31 | 1.3 | 30 | 4.4 | 1 | - |
| 12 | 26 | 52 | 88 | 36 | 1.5 | 35 | 5.3 | 1 | - |
| 13 | 30 | 52.8 | 88 | 36 | 1.5 | 35 | 5.3 | 1 | - |
| 14 | 37 | 70.4 | 100 | 41 | 1.7 | 40 | 6.0 | 1 | 1 |
| 15 | 45 | 83.2 | 100 | 41 | 1.7 | 40 | 6.0 | 1 | 1 |
| 16 | 55 | 104 | 114 | 47 | 2.0 | 46 | 6.8 | 1 | 1 |
| 17 | 63 | 124.8 | 120 | 49 | 2.1 | 48 | 7.2 | 1 | 1 |
| 18 | 75 | 145.6 | 134 | 55 | 2.3 | 54 | 8.0 | 1 | 1 |
| 19 | 90 | 166.4 | 138 | 56 | 2.4 | 55 | 8.3 | 1 | 1 |
| 20 | 110 | 208 | 152 | 62 | 2.6 | 61 | 9.1 | 1 | 1 |
| 21 | 132 | 249.6 | 166 | 67 | 2.8 | 66 | 10.0 | 1 | 1 |
| 22 | 160 | 291.2 | 178 | 72 | 3.1 | 71 | 10.7 | 1 | 1 |
| 23 | 180 | 332.8 | 192 | 78 | 3.3 | 77 | 11.5 | 1 | 1 |
| 24 | 200 | 374.4 | 202 | 82 | 3.5 | 81 | 12.1 | 1 | 1 |
| 25 | 250 | 457.6 | 228 | 92 | 3.9 | 91 | 13.7 | 1 | 1 |

Table 2.1D: SCHEDULE PROPOSED SOLAR PV ARRAY CAPACITY AND MODULE SELECTION

| Model # | Pump KW | PV Array kWp | Oversize factor | Selected Panel Wp | Total Panels | Panels per String | Total String | Combiner box for > 2 strings | Solar Inverter KW | Module Mount Structure |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 0.75 | 1.3 | 1.73 | 650 | 2 | 2 | 1 | n/a(Direct to invr) | 1.5 | 1 x 2MMS |
| 2 | 1.5 | 2.6 | 1.73 | 650 | 4 | 4 | 1 | n/a(Direct to invr) | 2.2 | 1 x 4MMS |
| 3 | 2.2 | 4.55 | 2.07 | 650 | 7 | 7 | 1 | n/a(Direct to invr) | 3.7 | 2 x 4MMS |
| 4 | 3.7 | 7.15 | 1.93 | 650 | 11 | 11 | 1 | n/a(Direct to invr) | 5.5 | 3 x 4MMS |
| 5 | 5.5 | 10.4 | 1.89 | 650 | 16 | 16 | 1 | n/a(Direct to invr) | 7.5 | 1 x16MMS |
| 6 | 7.5 | 15.6 | 2.08 | 650 | 24 | 12 | 2 | n/a(Direct to invr) | 11 | 3 x4MMS |
| 7 | 9.3 | 19.5 | 2.1 | 650 | 30 | 15 | 2 | n/a(Direct to invr) | 15 | 2 x16MMS |
| 8 | 11 | 20.8 | 1.89 | 650 | 32 | 16 | 2 | n/a(Direct to invr) | 15 | 2 x16MMS |
| 9 | 15 | 31.2 | 2.08 | 650 | 48 | 16 | 3 | 3 strings | 22 | 3 x16MMS |
| 10 | 18.5 | 39 | 2.11 | 650 | 60 | 15 | 4 | 4 strings | 26 | 4 x16MMS |
| 11 | 22 | 41.6 | 1.89 | 650 | 64 | 16 | 4 | 4 strings | 37 | 4 x16MMS |
| 12 | 26 | 52 | 2 | 650 | 80 | 16 | 5 | 5 strings | 37 | 5 x16MMS |
| 13 | 30 | 62.4 | 2.08 | 650 | 96 | 16 | 6 | 6 strings | 45 | 6 x16MMS |
| 14 | 37 | 72.8 | 1.97 | 650 | 112 | 16 | 7 | 7 strings | 45 | 7 x16MMS |
| 15 | 45 | 83.2 | 1.85 | 650 | 128 | 16 | 8 | 8 strings | 63 | 8 x16MMS |
| 16 | 55 | 104 | 1.89 | 650 | 160 | 16 | 10 | 10 strings | 75 | 10 x16MMS |
| 17 | 63 | 124.8 | 1.98 | 650 | 192 | 16 | 12 | 12 strings | 90 | 12 x16MMS |
| 18 | 75 | 145.6 | 1.94 | 650 | 224 | 16 | 14 | 14 strings | 110 | 14 x16MMS |
| 19 | 90 | 166.4 | 1.85 | 650 | 256 | 16 | 16 | 16 strings | 132 | 16 x16MMS |
| 20 | 110 | 208 | 1.89 | 650 | 320 | 16 | 20 | 20 strings | 160 | 20 x16MMS |
| 21 | 132 | 249.6 | 1.89 | 650 | 384 | 16 | 24 | 24 strings | 180 | 24 x16MMS |
| 22 | 160 | 291.2 | 1.82 | 650 | 448 | 16 | 28 | (14+14) string | 250 | 28 x16MMS |
| 23 | 180 | 332.8 | 1.85 | 650 | 512 | 16 | 32 | (16+16) string | 250 | 32 x16MMS |
| 24 | 200 | 374.4 | 1.87 | 650 | 576 | 16 | 36 | (18+18) string | 300 | 36 x16MMS |
| 25 | 250 | 457.6 | 1.83 | 650 | 704 | 16 | 44 | (22+22) string | 350 | 44 x16MMS |