## Sheet1
HDPE water pipes with accessories
# | Description | QTY
1 | HDPE, polyethylene pipe with diameter 32 mm (OD), rating SDR11. - Length of 50 m in coil. - Marking: pipe must be marked in compliance with ISO 4427. Suitable for use with compression fittings. - Suitable and designed for Butt Fusion Welding equipment. - Suitable for open-cut installation on a sand bed. - Colour for drinking water identification. Black with blue stripes, or blue with black stripes. - Comply with the ISO 4427/EN 12201 standards. - Temperature range up to 45 degrees Celsius. - UV-resistant, corrosion-free, flexible, suitable for buried installation. - Quality Assurance and Delivery: All pipes shall be delivered free from defects and accompanied by manufacturer certificates confirming compliance with the above-specified standards. | 20
2 | HDPE, Polyethylene pipe with diameter 50 mm (OD), rating SDR11. - Length of 50 m in coil. Marking: pipe must be marked in compliance with ISO 4427. - Suitable for use with compression fittings. - Suitable and designed for Butt Fusion Welding equipment. - Suitable for open-cut installation on a sand bed. - Colour for drinking water identification. Black with blue stripes, or blue with black stripes. - Comply with the ISO 4427/EN 12201 standards. - Temperature range up to 45 degrees Celsius. - UV-resistant, corrosion-free, flexible, suitable for buried installation. - Quality Assurance and Delivery: All pipes shall be delivered free from defects and accompanied by manufacturer certificates confirming compliance with the above-specified standards. | 60
3 | HDPE, Polyethylene pipe with diameter 90 mm (OD), rating SDR 11. - Pipe length of 12 m. Marking: pipe must be marked in compliance with ISO 4427. - Suitable for use with compression fittings. - Suitable and designed for Butt Fusion Welding equipment. - Suitable for open-cut installation on a sand bed. - Colour for drinking water identification. Black with blue stripes, or blue with black stripes. - Comply with the ISO 4427/EN 12201 standards. - Temperature range up to 45 degrees Celsius. - UV-resistant, corrosion-free, flexible, suitable for buried installation. - Quality Assurance and Delivery: All pipes shall be delivered free from defects and accompanied by manufacturer certificates confirming compliance with the above-specified standards. | 2375
4 | HDPE, Polyethylene pipe with diameter 160 mm (OD), rating SDR 17. - Pipe length of 12 m. Marking: pipe must be marked in compliance with ISO 4427. - Suitable for use with compression fittings. - Suitable and designed for Butt Fusion Welding equipment. - Suitable for open-cut installation on a sand bed. - Colour for drinking water identification. Black with blue stripes, or blue with black stripes. - Comply with the ISO 4427/EN 12201 standards. - Temperature range up to 45 degrees Celsius. - UV-resistant, corrosion-free, flexible, suitable for buried installation. - Quality Assurance and Delivery: All pipes shall be delivered free from defects and accompanied by manufacturer certificates confirming compliance with the above-specified standards. | 1000
5 | HDPE Clamp Saddle (160 mm to 90mm), PN16: If item 5 selected item 6 will not be procured | 90
6 | Spigot Reducing Tees (160 mm to 90 mm), PN16: if item 6 selected item 5 will not be procured | 90
7 | End cap OD 160 mm, PN16 | 6
8 | Isolation Gate valves DN160, PN16 (manual wheel for slow closing, full bore/unobstructed passage). To include flanged stub ends, and all other accessories, to fit OD160/SDR17 pipeline. To comply with ISO 16631. Ductile Iron. | 15
9 | Air Release valves (Automatic DN50) – OD160 mm PN16. | 15
10 | Washout valves (Gate 150/150) PN16. | 6
11 | Elbow 45 degrees OD 160 mm, PN16 | 6
12 | DN90 (3-inch) Resilient Seated Gate Valves, PN16. To include all components to connect at both ends to OD 90mm SDR11, such as Ductile Iron Backing Rings, and Stub Ends (Flange Adapters). To comply with ISO 16631. | 80
13 | Ball Valve, Compression, 90mm, PE100, PN16 | 70
14 | Elbow, 90° (degrees), 90mm Compression, PN16, PE100 | 100
15 | Flowmeter, 90mm Compression, PN16, PE100 | 90
16 | Reducer, Compression, 90-50mm, PN16, PE100 | 50
17 | Tee, equal, Compression 90mm, PN16, PE100 | 5
18 | Tee, Reduced Branch, Compression, 90-50mm, PN16, PE100 | 30
19 | Ball Valve, Compression, 50mm, PN16, PE100 | 31
20 | Reducer, Compression, 50-32mm, PN16, PE100 | 70
21 | Tee, Equal, Compression, 50mm, PN16, PE100 | 7
22 | Non-return valve, 90mm, PN16, PE100 | 10
Requirements:
R1 | Manufacturing certificate, and proof of origin (brand, factory name, and address) to be provided with bid.
R2 | Catalogue with detailed specifications of the requested products to be provided with bid.
R3 | Samples of pipes and pipe accessories are to be provided upon request.
R4 | Inspection of factory, warehouse, and pipes by UNICEF and its representatives is to be facilitated on request.
R5 | All pipes and accessories to comply with: High Density Polyethylene PE100 grade (HDPE). - All fittings are Compression. - Suitable and designed for Butt Fusion Welding equipment. - Suitable for open-cut installation on a sand bed. - Marking: pipe must be marked in compliance with ISO 4427. - Comply with the ISO 4427/EN 12201 standards. - Temperature range up to 45 degrees Celsius. - UV-resistant, corrosion-free, flexible, suitable for buried installation. - Quality Assurance and Delivery: All pipes shall be delivered free from defects and accompanied by manufacturer certificates confirming compliance with the above-specified standards.
R6 | Industry standards and certifications: All pipes are to be manufactured, tested, and certified in compliance with ISO 4427-2 (or the harmonised equivalent EN 12201-2 (European), and TS 418-2 (Turkish) standards). An internationally accepted alternative is NSF 61 certification.
R7 | Factory and production requirement (including for raw materials): Manufacturing of HDPE pipes and accessories according to EN 12201-1 (part 1), ISO 4427 and DIN 8074 under the control of ISO 9001:2008. Certificate to be provided to ascertain conformance with ISO 9001.
R8 | Mandatory Testing Procedures Under TS 418-2 (Turkish standards) or EN 12201-2,part 2 (European Standard). Bidder to provide detailed description of periodic material testing during production, type of tests and parameters, and to which industry standards. Tests to include, but not limited to: 1: Geometrical and physical properties (Dimensional Verification, Ovality, MFR); 2: Mechanical and Hydrostatic testing; 3: Material Integrity and Performance tests.
R9 | Bidder to provide Type Test Reports (TT): For demonstrating pipe lines successfully passed the 1,000-hour pressure test within the last 12 months.
R10 | Third-Party Product Conformity Certification: Provide name of an accredited body (preferred are: Kiwa, DVGW, TSE, SGS, or Bureau Veritas) explicitly naming ISO 4427-2 or EN 12201-2. ISO 4427: Certify polyethylene piping systems for water supply applications. ISO 4427 ensures PE pipes and fittings meet international quality and performance standards.
R11 | The OD 90mm pipes (1,000 units) to be nested inside the OD160mm pipe (1,000 units), for space saving during transport.
R12 | Warranty period for material defects for all products of 5 years.